## GS20 & 30 Quick REF
GS20/30 PARAMETER SUMMARY |  |  |  | GS2 Equivalent PARAMETER SUMMARY |  | GS3 Equivalent PARAMETER SUMMARY |  | GS4 Equivalent PARAMETER SUMMARY |  | SORT ODER BY ANY DRIVE TYPE | SEE DISCLAIMER
GS20/30 Seq | GS20/30 Parameter Group | GS20/30 Pr.No. | GS20/30 Parameter Description | GS2 Pr. No. | GS2 Parameter Description | GS3 Pr. No. | GS3 Parameter Description | GS4 Pr. No. | GS4 Parameter Description
1 | P00 Drive | P00.00 | GS20/30 Model ID- Identity Code | P9.42 | Manufacturer Model Information | P9.41 & 42 | Manufacturer Model Information | P09.42 | GS Model ID
2 | P00 Drive | P00.01 | Rated Current |  |  |  |  | P09.33 | GS4 Drive Rated Amps
3 | P00 Drive | P00.02 | Restore to Default | P9.07 P9.08 | Parameter Lock Restore to Default | P9.07 P9.08 | Parameter Lock Restore to Default | P09.07 P09.08 | Parameter Lock Restore to Default
4 | P00 Drive | P00.03 | Start-up display Selection |  |  |  |  | P08.01 | Start-up Display Selection
5 | P00 Drive | P00.04 | User Display | P8.00 | User Defined Display Function | P8.00 | User Defined Display Function | P08.00 | User Display
6 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | P8.01 | Frequency Scale Factor | P8.01 | Frequency Scale Factor | P08.05 | Output Frequency Gain
7 | P00 Drive | P00.06 | Firmware version | P9.39 | Firmware Version | P9.39 | Firmware Version | P09.39 | Firmware version
8 | P00 Drive | P00.07 | Parameter protection password input |  |  |  |  | P08.06 | Password Input
9 | P00 Drive | P00.08 | Parameter protection password setting |  |  |  |  | P08.07 | Password Set Up
10 | P00 Drive | P00.10 | Control Method- Torq or Speed
11 | P00 Drive | P00.11 | Speed (Velocity) Control mode | P2.00 | Volts/Hertz Settings | P2.00 & P2.10 | Volts/Hertz Settings & Control Mode | P02.11 | Control Mode
12 | P00 Drive | P00.16 | Torque duty selection |  |  |  |  | P06.34 | Variable/Constant Torque Duty Selection
13 | P00 Drive | P00.17 | Carrier frequency | P2.08 | PWM Carrier Frequency | P2.08 | PWM Carrier Frequency | P02.10 | PWM Carrier Frequency
14 | P00 Drive | P00.19 | PLC command mask |  |  |  |  | P09.34 | PLC Command Mask (status only)
15 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | P4.00 | Source of Frequency Command | P4.00 | Source of Frequency Command | P04.00 | 1st Source of Frequency Command [Remote]
16 | P00 Drive | P00.21 | Operation command source (AUTO, REMOTE) | P3.00 | Source of Operation Command | P3.00 | Source of Operation Command | P03.00 | 1st Source of Operation Command [Remote]
17 | P00 Drive | P00.22 | Stop method | P1.00 | Stop Methods | P1.00 | Stop Methods | P01.00 | Stop Method
18 | P00 Drive | P00.23 | Motor direction control | P6.03 | Reverse Operation Inhibit | P6.03 | Reverse Operation Inhibit | P06.09 | Fwd/Rev Direction Inhibit
19 | P00 Drive | P00.24 | Digital operator (keypad) frequency command memory
20 | P00 Drive | P00.25 | User-defined characteristics (COEFF ATT) |  |  |  |  | P08.02 | User Defined Format
21 | P00 Drive | P00.26 | User-defined maximum value (COEFF MAX) | P7.01 | PV 100% Value | P7.01 | PV 100% Value | P08.03 | User Defined Max
22 | P00 Drive | P00.27 | User-defined value (COEFF SET) |  |  |  |  | P08.04 | User Defined Setpoint
23 | P00 Drive | P00.29 | LOCAL / REMOTE selection |  |  |  |  | P03.58 | Local/Remote Switch Mode
24 | P00 Drive | P00.30 | Master frequency command source (HAND, LOCAL) | P4.00 | Source of Frequency Command | P4.13 | 2nd Source of Frequency Command [Local] | P04.01 | 2nd Source of Frequency Command [Local]
25 | P00 Drive | P00.31 | Operation command source (HAND, LOCAL) | P3.00 | Source of Operation Command | P3.01 - .10 & P03.31 | 2nd Source of Frequency Command [Local] | P03.01 | 2nd Source of Operation Command [Local]
26 | P00 Drive | P00.32 | Digital keypad STOP function | P3.00 | Source of Operation Command | P3.01 - .10 & P03.31 | 2nd Source of Frequency Command [Local]
27 | P00 Drive | P00.35 | Auxiliary frequency source
28 | P00 Drive | P00.36 | Master and auxiliary frequency command selection
29 | P00 Drive | P00.48 | Display filter time (current)
30 | P00 Drive | P00.49 | Display filter time (keypad)
31 | P00 Drive | P00.50 | Date Code of Software version (date)
32 | P01 Basic | P01.00 | Maximum operation frequency | P0.04 | Motor Maximum RPM | P0.04 | Motor Maximum RPM | P0.04 | Drive Maximum Output Frequency
33 | P01 Basic | P01.01 | Motor 1 Fbase | P0.02 | Motor Base Frequency | P0.02 | Motor Base Frequency | P0.02 | Motor 1 Base Frequency
34 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | P0.00 | Motor Nameplate Voltage | P0.00 | Motor Nameplate Voltage | P0.00 | Motor 1 Maximum Output Voltage
35 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | P2.04 | Mid-point Frequency | P2.04 | Mid-point Frequency | P02.04 | Motor 1 Middle Output Frequency 1
36 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | P2.05 | Mid-point Voltage | P2.05 | Mid-point Voltage | P02.05 | Motor 1 Middle Output Voltage 1
37 | P01 Basic | P01.05 | Motor 1, Mid-point frequency 2 |  |  |  |  | P02.06 | Motor 1 Middle Output Frequency 2
38 | P01 Basic | P01.06 | Motor 1, Mid-point voltage 2 |  |  |  |  | P02.07 | Motor 1 Middle Output Voltage 2
39 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | P2.06 | Min. Output Frequency | P2.06 | Min. Output Frequency | P02.08 | Motor 1 Minimum Output Frequency
40 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | P2.07 | Min. Output Voltage | P2.07 | Min. Output Voltage | P02.09 | Motor 1 Minimum Output Voltage
41 | P01 Basic | P01.09 | Start-up frequency |  |  |  |  | P02.19 | Start Frequency
42 | P01 Basic | P01.10 | Output frequency upper limit | P6.15 | Upper Bound of Output Frequency | P6.15 | Upper Bound of Output Frequency | P06.25 | Upper Limit of Output Frequency
43 | P01 Basic | P01.11 | Output frequency lower limit | P6.16 | Lower Bound of Output Frequency | P6.16 | Lower Bound of Output Frequency | P06.26 | Lower Limit of Output Frequency
44 | P01 Basic | P01.12 | Acceleration time 1 | P1.01 | Acceleration Time 1 | P1.01 | Acceleration Time 1 | P01.01 | Acceleration Time 1
45 | P01 Basic | P01.13 | Deceleration time 1 | P1.02 | Deceleration Time 1 | P1.02 | Deceleration Time 1 | P01.02 | Deceleration Time 1
46 | P01 Basic | P01.14 | Acceleration time 2 | P1.05 | Acceleration Time 2 | P1.05 | Acceleration Time 2 | P01.03 | Acceleration Time 2
47 | P01 Basic | P01.15 | Deceleration time 2 | P1.06 | Deceleration Time 2 | P1.06 | Deceleration Time 2 | P01.04 | Deceleration Time 2
48 | P01 Basic | P01.16 | Acceleration time 3 |  |  |  |  | P01.05 | Acceleration Time 3
49 | P01 Basic | P01.17 | Deceleration time 3 |  |  |  |  | P01.06 | Deceleration Time 3
50 | P01 Basic | P01.18 | Acceleration time 4 | P1.08 | Accel 1 to Accel 2 frequency transition | P1.08 | Accel 1 to Accel 2 frequency transition | P01.07 | Acceleration Time 4
51 | P01 Basic | P01.19 | Deceleration time 4 | P1.08 | Accel 1 to Accel 2 frequency transition | P1.08 | Accel 1 to Accel 2 frequency transition | P01.08 | Deceleration Time 4
52 | P01 Basic | P01.20 | JOG acceleration time |  |  |  |  | P01.13 | Jog Acceleration Time
53 | P01 Basic | P01.21 | JOG deceleration time |  |  |  |  | P01.14 | Jog Deceleration Time
54 | P01 Basic | P01.22 | JOG frequency | P5.00 | Jog | P5.00 | Jog | P05.00 | Jog Frequency
55 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | P1.08 P1.09 | Accel 1 to Accel 2 frequency transition Decel 2 to Decel 1 frequency transition. | P1.07 P1.08 P1.09 | Accel 1 to Accel 2 frequency transition Decel 2 to Decel 1 frequency transition. | P01.16 P01.17 P01.18 | Accel/Decel Transition Method Accel Trans Freq Decel Trans Freq
56 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P1.03 | Accel S-curve | P1.03 | Accel S-curve | P01.09 | S-curve Accel Time 1
57 | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P1.03 | Accel S-curve | P1.03 | Accel S-curve | P01.11 | S-curve Accel Time 2
58 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P1.04 | Decel S-curve | P1.04 | Decel S-curve | P01.10 | S-curve Decel Time 1
59 | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P1.04 | Decel S-curve | P1.04 | Decel S-curve | P01.12 | S-curve Decel Time 2
60 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | P1.10 | Skip Frequency 1 | P1.10 | Skip Frequency 1 | P01.19 | Skip Frequency 1 Upper Limit
61 | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | P1.10 | Skip Frequency 1 | P1.10 | Skip Frequency 1 | P01.20 | Skip Frequency 1 Lower Limit
62 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | P1.11 | Skip Frequency 2 | P1.11 | Skip Frequency 2 | P01.21 | Skip Frequency 2 Upper Limit
63 | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | P1.11 | Skip Frequency 2 | P1.11 | Skip Frequency 2 | P01.22 | Skip Frequency 2 Lower Limit
64 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | P1.12 | Skip Frequency 3 | P1.12 | Skip Frequency 3 | P01.23 | Skip Frequency 3 Upper Limit
65 | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | P1.12 | Skip Frequency 3 | P1.12 | Skip Frequency 3 | P01.24 | Skip Frequency 3 Lower Limit
66 | P01 Basic | P01.34 | Zero-speed mode |  |  |  |  | P02.18 | Zero Speed Select
67 | P01 Basic | P01.35 | Motor 2, Output frequency (Base frequency / Motor's rated frequency) |  |  |  |  | P0.13 | Motor 2 Base Frequency
68 | P01 Basic | P01.36 | Motor 2, Output voltage (Base voltage / Motor's rated voltage) |  |  |  |  | P0.11 | Motor 2 Maximum Output Voltage
69 | P01 Basic | P01.37 | Motor 2, Mid-point frequency |  |  |  |  | P02.12 | Motor 2 Middle Output Frequency 1
70 | P01 Basic | P01.38 | Motor 2, Mid-point voltage 1 |  |  |  |  | P02.13 | Motor 2 Middle Output Voltage 1
71 | P01 Basic | P01.39 | Motor 2, Mid-point frequency 2 |  |  |  |  | P02.14 | Motor 2 Middle Output Frequency 2
72 | P01 Basic | P01.40 | Motor 2, Mid-point voltage 2 |  |  |  |  | P02.15 | Motor 2 Middle Output Voltage 2
73 | P01 Basic | P01.41 | Motor 2, Minimum output frequency |  |  |  |  | P02.16 | Motor 2 Minimum Output Frequency
74 | P01 Basic | P01.42 | Motor 2, Minimum output voltage |  |  |  |  | P02.17 | Motor 2 Minimum Output Voltage
75 | P01 Basic | P01.43 | V/F curve selection | P2.00 | Volts/Hertz Settings | P2.00 | Volts/Hertz Settings | P02.00 | Volts/Hertz Settings
76 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | P6.06 | Auto Adjustable Accel/Decel | P6.06 | Auto Adjustable Accel/Decel | P06.13 | Auto Adjustable Accel/ Decel
77 | P01 Basic | P01.45 | Time unit for accel/decel and S-curve |  |  |  |  | P01.15 | Time Unit for Accel/Decel & S-curve
78 | P01 Basic | P01.49 | Regenerative energy restriction control (decel method) |  |  |  |  | P01.29 | Deceleration Method
79 | P01 Basic | P01.52 | Motor 2, Maximum operation frequency
80 | P01 Basic | P01.53 | Motor 3, Maximum operation frequency
81 | P01 Basic | P01.54 | Motor 3, Output frequency (Base frequency / Motor's rated frequency)
82 | P01 Basic | P01.55 | Motor 3, Output voltage (Base voltage / Motor's rated voltage)
83 | P01 Basic | P01.56 | Motor 3, Mid-point frequency 1
84 | P01 Basic | P01.57 | Motor 3, Mid-point voltage 1
85 | P01 Basic | P01.58 | Motor 3, Mid-point frequency 2
86 | P01 Basic | P01.59 | Motor 3, Mid-point voltage 2
87 | P01 Basic | P01.60 | Motor 3, Minimum output frequency
88 | P01 Basic | P01.61 | Motor 3, Minimum output voltage
89 | P01 Basic | P01.62 | Motor 4, Maximum operation frequency
90 | P01 Basic | P01.63 | Motor 4, Output frequency (Base frequency / Motor's rated frequency)
91 | P01 Basic | P01.64 | Motor 4, Output voltage (Base voltage / Motor's rated voltage)
92 | P01 Basic | P01.65 | Motor 4, Mid-point frequency 1
93 | P01 Basic | P01.66 | Motor 4, Mid-point voltage 1
94 | P01 Basic | P01.67 | Motor 4, Mid-point frequency 2
95 | P01 Basic | P01.68 | Motor 4, Mid-point voltage 2
96 | P01 Basic | P01.69 | Motor 4, Minimum output frequency
97 | P01 Basic | P01.70 | Motor 4, Minimum output voltage
98 | P02 Digital IO | P02.00 | Two-wire / three- wire operation control | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.02 | 2/3 Wire Operation Mode
99 | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.03 | Multi-Function Input (DI1)
100 | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P3.01 | Multi-function Input Terminals (DI1 - DI2) | P03.04 | Multi-Function Input (DI2)
101 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | P3.02 | Multi-function Input (DI3) | P3.02 | Multi-function Input (DI3) | P03.05 | Multi-Function Input (DI3)
102 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | P3.03 | Multi-function Input (DI4) | P3.03 | Multi-function Input (DI4) | P03.06 | Multi-Function Input (DI4)
103 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | P3.04 | Multi-function Input (DI5) | P3.04 | Multi-function Input (DI5) | P03.07 | Multi-Function Input (DI5)
104 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | P3.05 | Multi-function Input (DI6) | P3.05 | Multi-function Input (DI6) | P03.08 | Multi-Function Input (DI6)
105 | P02 Digital IO | P02.07 | Multi-function input command 7 (DI7) |  |  | P3.06 | Multi-function Input (DI7) | P03.09 | Multi-Function Input (DI7)
106 | P02 Digital IO | P02.09 | UP / DOWN key mode |  |  |  |  | P03.39 | Increase/Decrease Speed Mode
107 | P02 Digital IO | P02.10 | Constant speed, accel/decele speed of UP/DOWN Key |  |  |  |  | P03.40 | DI6 Counter Debounce Filter
108 | P02 Digital IO | P02.11 | Multi-function input response time |  |  |  |  | P03.41 | Digital Input Response Time
109 | P02 Digital IO | P02.12 | Multi-function input mode selection |  |  |  |  | P03.42 | Multi-Function Input Contact Selection (0=N.O. / 1=N.C.)
110 | P02 Digital IO | P02.13 | Multi-function output 1 (R1) | P3.11 | Multi-Function Output Terminal 1 | P3.11 | Multi-Function Output Terminal 1 | P03.17 | Multi-Function Output Terminal 1 (Relay 1 or PLC Y0)
111 | P02 Digital IO | P02.16 | Multi-function output 2 (DO1) | P3.12 | Multi-Function Output Terminal 2 | P3.12 | Multi-Function Output Terminal 2 | P03.19 | Multi-Function Output Terminal 3 (DO1 or PLC Y3)
112 | P02 Digital IO | P02.17 | Multi-function output 3 (DO2) |  |  | P3.13 | Multi-Function Output Terminal 3 | P03.20 | Multi-Function Output Terminal 4 (DO2 or PLC Y4)
113 | P02 Digital IO | P02.18 | Multi-function output direction ACT |  |  |  |  | P03.43 | Multi-Function Output Contact Selection (0=N.O. / 1=N.C.)
114 | P02 Digital IO | P02.19 | Terminal counting value reached (returns to 0) |  |  |  |  | P03.44 | Final Counter Value
115 | P02 Digital IO | P02.20 | Preliminary (Middle) counting value reached (does not return to 0) |  |  |  |  | P03.45 | Mid-point Counter Value
116 | P02 Digital IO | P02.21 | Digital output gain (DO) |  |  |  |  | P03.38 | Frequency Output (FO) Scaling Factor
117 | P02 Digital IO | P02.22 | Desired frequency reached 1 | P3.16 | Desired Frequency | P3.16 | Desired Frequency 1 | P03.32 | Desired Frequency 1
118 | P02 Digital IO | P02.23 | The bandwidth of the desired frequency reached 1 |  |  |  |  | P03.33 | Desired Frequency 1 Width
119 | P02 Digital IO | P02.24 | Desired frequency reached 2 |  |  | P3.20 | Desired Frequency 2 | P03.34 | Desired Frequency 2
120 | P02 Digital IO | P02.25 | bandwidth of desired freq reached 2 |  |  |  |  | P03.35 | Desired Frequency 2 Width
121 | P02 Digital IO | P02.34 | Output frequency setting for digital output terminal |  |  |  |  | P03.53 | Output Frequency Threshold for Multi- Function Output Terminals
122 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | P6.30 | Line Start Lockout | P6.30 | Line Start Lockout | P06.29 | Line Start Lockout
123 | P02 Digital IO | P02.36 | GS30 Only DO10 |  |  | P3.14 | Digital Output 4
123 | P02 Digital IO | P02.37 | GS30 Only DO11
123 | P02 Digital IO | P02.47 | Motor RPM zero- speed level
124 | P02 Digital IO | P02.50 | Display the status of multi-function input terminals DI1-DI7 |  |  |  |  | P03.46 | Digital Input Active Status
125 | P02 Digital IO | P02.51 | Display the status of multi-function output terminals R1, DO1, DO2 |  |  |  |  | P03.47 | Digital Output Active Status
126 | P02 Digital IO | P02.52 | Display the external multi-function input terminals DI1-DI7 used by PLC |  |  |  |  | P03.48 | PLC – Digital Input Mask
127 | P02 Digital IO | P02.53 | Display the external multi-function output terminals R1, DO1, DO2 used by PLC |  |  |  |  | P03.49 | PLC – Digital Output Mask
128 | P02 Digital IO | P02.54 | Display the frequency command executed by external terminal (EXT Speed REC) |  |  |  |  | P03.50 | Increase/Decrease Speed Command Record
129 | P02 Digital IO | P02.58 | Multi-function output terminal (function 42): brake frequency check point
130 | P02 Digital IO | P02.78 | Motor deceleration gear ratio
131 | P02 Digital IO | P02.79 | Automatic index positioning angle setting
132 | P02 Digital IO | P02.80 | Automatic index positioning deceleration time
133 | P02 Digital IO | P02.81 | EF activates when the terminal count value reached
134 | P02 Digital IO | P02.82 | Initial Frequency com-mand (F) mode after stop
135 | P02 Digital IO | P02.83 | Initial Frequency com-mand (F) setting after stop
136 | P03 Analog IO | P03.00 | Analog input selection (AI1) |  |  |  |  | P04.02 | Analog Input 1 (AI1) Function
137 | P03 Analog IO | P03.01 | Analog input selection (AI2) | P4.00 | Source of Frequency Command | P4.00 | Source of Frequency Command | P04.03 | Analog Input 2 (AI2) Function
138 | P03 Analog IO | P03.03 | Analog input bias (AI1) |  |  |  |  | P04.10 | AI1 Input Bias (Offset)
139 | P03 Analog IO | P03.04 | Analog input bias (AI2) | P4.02 | Analog Input Offset | P4.02 | Analog Input Offset | P04.15 | AI2 Input Bias (Offset)
140 | P03 Analog IO | P03.07 | Positive / negative bias mode (AI1) |  |  |  |  | P04.11 | AI1 Input Bias (Offset) Polarity
141 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) | P4.01 | Analog Input Offset Polarity | P4.01 | Analog Input Offset Polarity | P04.16 | AI2 Input Bias (Offset) Polarity
142 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | P4.04 | Analog Input Reverse Motion Enable | P4.04 | Analog Input Reverse Motion Enable | P04.09 | Analog Frequency Command for Reverse Run
143 | P03 Analog IO | P03.11 | Analog input gain (AI1) |  |  |  |  | P04.12 | AI1 Input Gain
144 | P03 Analog IO | P03.12 | Analog input gain (AI2) | P4.03 | Analog Input Gain | P4.03 | Analog Input Gain | P04.17 | AI2 Input Gain
145 | P03 Analog IO | P03.15 | Analog input filter (LPF) time (AI1) |  |  |  |  | P04.13 | AI1 Filter
146 | P03 Analog IO | P03.16 | Analog input filter (LPF) time (AI2) |  |  |  |  | P04.18 | AI2 Filter
147 | P03 Analog IO | P03.18 | Analog input addition function
148 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | P4.05 | Loss of ACI Signal (4-20mA) | P4.05 | Loss of ACI Signal (4-20mA) | P04.64 | Loss of AI2 Signal (4~20mA)
149 | P03 Analog IO | P03.20 | Multi-function output (A01) | P4.11 | Analog Output Signal | P4.11 | Analog Output Signal | P04.50 | Analog Output 1 (AO1)
150 | P03 Analog IO | P03.21 | Analog output gain (A01) | P4.12 | Analog Output Gain | P4.12 | Analog Output Gain | P04.51 | AO1 Gain
151 | P03 Analog IO | P03.22 | Analog output in REV direction (A01) |  |  |  |  | P04.52 | AO1 Negative Value Handle
152 | P03 Analog IO | P03.27 | A01 output bias
153 | P03 Analog IO | P03.28 | AI1 terminal input selection |  |  |  |  | P04.05 | AI1 – I/V Selection
154 | P03 Analog IO | P03.29 | AI2 terminal input selection |  |  |  |  | P04.06 | AI2 – I/V Selection
155 | P03 Analog IO | P03.30 | PLC analog output terminal status |  |  |  |  | P04.62 | PLC Analog Output Mask
156 | P03 Analog IO | P03.31 | A01 output selection |  |  |  |  | P04.53 | AO1 0~20mA/4~20mA Selection
157 | P03 Analog IO | P03.32 | A01 DC output setting level |  |  |  |  | P04.60 | AO1 Output Constant Level
158 | P03 Analog IO | P03.35 | A01 output filter time
159 | P03 Analog IO | P03.39 | VR (keypad dial) input selection
160 | P03 Analog IO | P03.40 | VR (keypad dial) input bias
161 | P03 Analog IO | P03.41 | VR (keypad dial) positive / negative bias
162 | P03 Analog IO | P03.42 | VR (keypad dial) gain
163 | P03 Analog IO | P03.43 | VR (keypad dial) filter time
164 | P03 Analog IO | P03.44 | Multi-function output (DO) by AI level source
165 | P03 Analog IO | P03.45 | AI upper level
166 | P03 Analog IO | P03.46 | AI lower level
167 | P03 Analog IO | P03.50 | Analog input curve calculation selection |  |  |  |  | P04.24 | AI V/Hz Calculated Selection
168 | P03 Analog IO | P03.57 | AI2 lowest point |  |  |  |  | P04.31 | AI2 Low V/A
169 | P03 Analog IO | P03.58 | AI2 proportional lowest point |  |  |  |  | P04.32 | AI2 Low Hz Percent
170 | P03 Analog IO | P03.59 | AI2 mid-point |  |  |  |  | P04.33 | AI2 Mid V/A
171 | P03 Analog IO | P03.60 | AI2 proportional mid- point |  |  |  |  | P04.34 | AI2 Mid Hz Percent
172 | P03 Analog IO | P03.61 | AI2 highest point |  |  |  |  | P04.35 | AI2 High V/A
173 | P03 Analog IO | P03.62 | AI2 proportional highest point |  |  |  |  | P04.36 | AI2 High Hz Percent
174 | P03 Analog IO | P03.63 | AI1 voltage lowest point |  |  |  |  | P04.25 | AI1 Low V/A
175 | P03 Analog IO | P03.64 | AI1 proportional lowest point |  |  |  |  | P04.26 | AI1 Low Hz Percent
176 | P03 Analog IO | P03.65 | AI1 voltage mid-point |  |  |  |  | P04.27 | AI1 Mid V/A
177 | P03 Analog IO | P03.66 | AI1 proportional mid- point |  |  |  |  | P04.28 | AI1 Mid Hz Percent
178 | P03 Analog IO | P03.67 | AI1 voltage highest point |  |  |  |  | P04.29 | AI1 High V/A
179 | P03 Analog IO | P03.68 | AI1 proportional highest point |  |  |  |  | P04.30 | AI1 High Hz Percent
180 | P03 Analog IO | P03.69 | Negative AI1 voltage highest point |  |  |  |  | P04.43 | -AI3 High Voltage Bipolar
181 | P03 Analog IO | P03.70 | Negative AI1 proportional highest point |  |  |  |  | P04.44 | -AI3 High Hz Percent Bipolar
182 | P03 Analog IO | P03.71 | Negative AI1 voltage mid-point |  |  |  |  | P04.45 | -AI3 Mid Voltage Bipolar
183 | P03 Analog IO | P03.72 | Negative AI1 proportional mid-point |  |  |  |  | P04.46 | -AI3 Mid Hz Percent Bipolar
184 | P03 Analog IO | P03.73 | Negative AI1 voltage lowest point |  |  |  |  | P04.47 | -AI3 Low Voltage Bipolar
185 | P03 Analog IO | P03.74 | Negative AI1 proportional lowest point |  |  |  |  | P04.48 | -AI3 Low Hz Percent Bipolar
186 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | P5.01 | Multi-Speed 1 | P5.01 | Multi-Speed 1 | P05.01 | Multi-Speed 1
187 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | P5.02 | Multi-Speed 2 | P5.02 | Multi-Speed 2 | P05.02 | Multi-Speed 2
188 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | P5.03 | Multi-Speed 3 | P5.03 | Multi-Speed 3 | P05.03 | Multi-Speed 3
189 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | P5.04 | Multi-Speed 4 | P5.04 | Multi-Speed 4 | P05.04 | Multi-Speed 4
190 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | P5.05 | Multi-Speed 5 | P5.05 | Multi-Speed 5 | P05.05 | Multi-Speed 5
191 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | P5.06 | Multi-Speed 6 | P5.06 | Multi-Speed 6 | P05.06 | Multi-Speed 6
192 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | P5.07 | Multi-Speed 7 | P5.07 | Multi-Speed 7 | P05.07 | Multi-Speed 7
193 | P04 Multi Step Spd | P04.07 | 8th step speed frequency |  |  | P5.08 | Multi-Speed 8 | P05.08 | Multi-Speed 8
194 | P04 Multi Step Spd | P04.08 | 9th step speed frequency |  |  | P5.09 | Multi-Speed 9 | P05.09 | Multi-Speed 9
195 | P04 Multi Step Spd | P04.09 | 10th step speed frequency |  |  | P5.10 | Multi-Speed 10 | P05.10 | Multi-Speed 10
196 | P04 Multi Step Spd | P04.10 | 11th step speed frequency |  |  | P5.11 | Multi-Speed 11 | P05.11 | Multi-Speed 11
197 | P04 Multi Step Spd | P04.11 | 12th step speed frequency |  |  | P5.12 | Multi-Speed 12 | P05.12 | Multi-Speed 12
198 | P04 Multi Step Spd | P04.12 | 13th step speed frequency |  |  | P5.13 | Multi-Speed 13 | P05.13 | Multi-Speed 13
199 | P04 Multi Step Spd | P04.13 | 14th step speed frequency |  |  | P5.14 | Multi-Speed 14 | P05.14 | Multi-Speed 14
200 | P04 Multi Step Spd | P04.14 | 15th step speed frequency |  |  | P5.15 | Multi-Speed 15 | P05.15 | Multi-Speed 15
201 | P04 Multi Step Spd | P04.50 | PLC buffer 0 |  |  |  |  | P08.20 | PLC Buffer 1
202 | P04 Multi Step Spd | P04.51 | PLC buffer 1 |  |  |  |  | P08.21 | PLC Buffer 2
203 | P04 Multi Step Spd | P04.52 | PLC buffer 2 |  |  |  |  | P08.22 | PLC Buffer 3
204 | P04 Multi Step Spd | P04.53 | PLC buffer 3 |  |  |  |  | P08.23 | PLC Buffer 4
205 | P04 Multi Step Spd | P04.54 | PLC buffer 4 |  |  |  |  | P08.24 | PLC Buffer 5
206 | P04 Multi Step Spd | P04.55 | PLC buffer 5 |  |  |  |  | P08.25 | PLC Buffer 6
207 | P04 Multi Step Spd | P04.56 | PLC buffer 6 |  |  |  |  | P08.26 | PLC Buffer 7
208 | P04 Multi Step Spd | P04.57 | PLC buffer 7 |  |  |  |  | P08.27 | PLC Buffer 8
209 | P04 Multi Step Spd | P04.58 | PLC buffer 8 |  |  |  |  | P08.28 | PLC Buffer 9
210 | P04 Multi Step Spd | P04.59 | PLC buffer 9 |  |  |  |  | P08.29 | PLC Buffer 10
211 | P04 Multi Step Spd | P04.60 | PLC buffer 10 |  |  |  |  | P08.30 | PLC Buffer 11
212 | P04 Multi Step Spd | P04.61 | PLC buffer 11 |  |  |  |  | P08.31 | PLC Buffer 12
213 | P04 Multi Step Spd | P04.62 | PLC buffer 12 |  |  |  |  | P08.32 | PLC Buffer 13
214 | P04 Multi Step Spd | P04.63 | PLC buffer 13 |  |  |  |  | P08.33 | PLC Buffer 14
215 | P04 Multi Step Spd | P04.64 | PLC buffer 14 |  |  |  |  | P08.34 | PLC Buffer 15
216 | P04 Multi Step Spd | P04.65 | PLC buffer 15 |  |  |  |  | P08.35 | PLC Buffer 16
217 | P04 Multi Step Spd | P04.66 | PLC buffer 16 |  |  |  |  | P08.36 | PLC Buffer 17
218 | P04 Multi Step Spd | P04.67 | PLC buffer 17 |  |  |  |  | P08.37 | PLC Buffer 18
219 | P04 Multi Step Spd | P04.68 | PLC buffer 18 |  |  |  |  | P08.38 | PLC Buffer 19
220 | P04 Multi Step Spd | P04.69 | PLC buffer 19 |  |  |  |  | P08.39 | PLC Buffer 20
221 | P05 Motor | P05.00 | Motor parameter auto-tuning |  |  | P0.05 | Motor Auto Tune | P0.05 | Motor Auto Tune
222 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | P0.01 | Motor Nameplate Amps | P0.01 | Motor Nameplate Amps | P0.01 | Motor 1 Rated Current
223 | P05 Motor | P05.02 | Induction Motor 1, Rated power (kW) |  |  |  |  | P0.08 | Motor 1 Rated Horsepower (HP)
224 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | P0.03 | Motor Base RPM | P0.03 | Motor Base RPM | P0.03 | Motor 1 Rated RPM
225 | P05 Motor | P05.04 | Induction Motor 1, Number of poles |  |  |  |  | P0.09 | Motor 1 Number of Poles
226 | P05 Motor | P05.05 | Induction Motor 1, No-load amps |  |  | P0.07 | Motor No-Load Current | P0.07 | Motor 1 No-Load Current
227 | P05 Motor | P05.06 | Induction Motor 1, Stator resistance (Rs) |  |  | P0.06 | Motor Resistance | P0.06 | Motor 1 Resistance
228 | P05 Motor | P05.07 | Induction Motor 1, Rotor resistance (Rr)
229 | P05 Motor | P05.08 | Induction Motor 1, Magnetizing inductance (Lm)
230 | P05 Motor | P05.09 | Induction Motor 1, Stator inductance (Lx)
231 | P05 Motor | P05.13 | Induction Motor 2, Full-load amps |  |  |  |  | P0.12 | Motor 2 Rated Current
232 | P05 Motor | P05.14 | Induction Motor 2, Rated power (kW) |  |  |  |  | P0.17 | Motor 2 Rated Horsepower (HP)
233 | P05 Motor | P05.15 | Induction Motor 2, Rated speed (rpm) |  |  |  |  | P0.14 | Motor 2 Rated RPM
234 | P05 Motor | P05.16 | Induction Motor 2, Number of poles |  |  |  |  | P0.18 | Motor 2 Number of Poles
235 | P05 Motor | P05.17 | Induction Motor 2, No- load amps |  |  |  |  | P0.16 | Motor 2 No-Load Current
236 | P05 Motor | P05.18 | Induction Motor 2, Stator resistance (Rs) |  |  |  |  | P0.15 | Motor 2 Resistance
237 | P05 Motor | P05.19 | Induction Motor 2, Rotor resistance (Rr)
238 | P05 Motor | P05.20 | Induction Motor 2, Magnetizing inductance (Lm)
239 | P05 Motor | P05.21 | Induction Motor 2, Stator inductance (Lx)
240 | P05 Motor | P05.22 | Multi-motor (induction) selection |  |  |  |  | P0.10 | Motor 1 or 2 Selection
241 | P05 Motor | P05.23 | Frequency for Y-connection / fl-connection switch for an induction motor |  |  |  |  | P02.20 | Y-D Switching Frequency
242 | P05 Motor | P05.24 | Y-connection /fl-con switch for an ind motor |  |  |  |  | P02.21 | Y-D Switching Enable
243 | P05 Motor | P05.25 | Delay time for Y-connection /fl-connection switch for an induction motor |  |  |  |  | P02.22 | Delay Time for Y-D Switching
244 | P05 Motor | P05.26 | Accumulated Watt- second for a motor in low word (W-msec.)
245 | P05 Motor | P05.27 | Accumulated Watt- second for a motor in high word (W-sec.)
246 | P05 Motor | P05.28 | Accumulated Watt- hour for a motor (W-hour)
247 | P05 Motor | P05.29 | Accumulated Watt- hour for a motor in low word (kW-hour)
248 | P05 Motor | P05.30 | Accumulated Watt- hour for a motor in high word (MW-hour)
249 | P05 Motor | P05.31 | Accumulated motor operation time (Minutes) |  |  |  |  | P08.11 | Accumulative Motor Operation Time (minute)
250 | P05 Motor | P05.32 | Accumulated motor operation time (days) |  |  |  |  | P08.12 | Accumulative Motor Operation Time (day)
251 | P05 Motor | P05.33 | Induction motor (IM) or permanent magnet synchronous AC motor (PM) selection
252 | P05 Motor | P05.34 | Full-load current for a permanent magnet synchronous AC motor
253 | P05 Motor | P05.35 | Rated power for a permanent magnet synchronous AC motor
254 | P05 Motor | P05.36 | Rated speed for a permanent magnet synchronous AC motor
255 | P05 Motor | P05.37 | Number of poles for a permanent magnet synchronous AC motor
256 | P05 Motor | P05.39 | Stator resistance Rs for a permanent magnet synchronous AC motor
257 | P05 Motor | P05.40 | Permanent magnet synchronous AC motor Ld
258 | P05 Motor | P05.41 | Permanent magnet synchronous AC motor Lq
259 | P05 Motor | P05.43 | Ke parameter of a permanent magnet synchronous AC motor
260 | P05 Motor | P05.64 | Induction Motor 3, Full-load amps
261 | P05 Motor | P05.65 | Induction Motor 3, Rated power (kW)
262 | P05 Motor | P05.66 | Induction Motor 3, Rated speed (rpm)
263 | P05 Motor | P05.67 | Induction Motor 3, Number of poles
264 | P05 Motor | P05.68 | Induction Motor 3, No- load amps
265 | P05 Motor | P05.69 | Induction Motor 3, Stator resistance (Rs)
266 | P05 Motor | P05.70 | Induction Motor 4, Full-load amps
267 | P05 Motor | P05.71 | Induction Motor 4, Rated power for (kW)
268 | P05 Motor | P05.72 | Induction Motor 4, Rated speed (rpm)
269 | P05 Motor | P05.73 | Induction Motor 4, Number of poles
270 | P05 Motor | P05.74 | Induction Motor 4, No-load amps
271 | P05 Motor | P05.75 | Induction Motor 4, Stator resistance (Rs)
272 | P06 Protection | P06.00 | Low voltage level |  |  |  |  | P06.35 | Low Voltage Level
273 | P06 Protection | P06.01 | Over-voltage stall prevention | P6.05 | Over-Voltage Stall Prevention | P6.05 & P6.17 | Over-Voltage Stall Prevention | P06.11 P06.27 | Over-Voltage Stall Prevention Over-Voltage Stall Prev Level
274 | P06 Protection | P06.02 | Selection for over-voltage stall prevention |  |  |  |  | P06.12 | Selection for Over- voltage Stall Prevention
275 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) | P6.10 | Over-Current Stall Prevention during Acceleration | P6.10 | Over-Current Stall Prevention during Acceleration | P06.20 | Over-Current Stall Prevention Level During Accel
276 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) | P6.11 | Over-Current Stall Prevention during Operation | P6.11 | Over-Current Stall Prevention during Operation | P06.21 | Over-Current Stall Prevention Level During Operation
277 | P06 Protection | P06.05 | Acceleration / deceleration time selection for stall prevention at constant speed |  |  |  |  | P06.36 | OC Stall Preventation Accel/Decel Time Selection at Normal Speed
278 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | P6.07 | Over-Torque Detection Mode | P6.07 | Over-Torque Detection Mode | P06.14 | Over-Torque Detection Mode (OT1)
279 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | P6.08 | Over-Torque Detection Level | P6.08 | Over-Torque Detection Level | P06.15 | Over-Torque Detection Level (OT1)
280 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | P6.09 | Over-Torque Detection Time | P6.09 | Over-Torque Detection Time | P06.16 | Over-Torque Detection Time (OT1)
281 | P06 Protection | P06.09 | Over-torque detection selection (motor 2) |  |  |  |  | P06.17 | Over-Torque Detection Mode (OT2)
282 | P06 Protection | P06.10 | Over-torque detection level (motor 2) |  |  |  |  | P06.18 | Over-Torque Detection Level (OT2)
283 | P06 Protection | P06.11 | Over-torque detection time (motor 2) |  |  |  |  | P06.19 | Over-Torque Detection Time (OT2)
284 | P06 Protection | P06.12 | Current limit |  |  |  |  | P06.38 | Torque Limit (Current Limit)
285 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | P6.00 | Electronic Thermal Overload Relay | P6.00 | Electronic Thermal Overload Relay | P06.00 | Electronic Thermal Overload Relay (Motor 1) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
286 | P06 Protection | P06.14 | Electronic thermal relay action time 1 (motor 1) |  |  |  |  | P06.01 | Electronic Thermal Characteristic (Motor 1)
287 | P06 Protection | P06.15 | Temperature level overheat (OH) warning |  |  |  |  | P06.30 | Heat Sink OH Warning Level
288 | P06 Protection | P06.16 | Stall prevention limit level (Weak magnetic field current stall prevention level) |  |  |  |  | P06.37 | OC Stall Preventation Limit for operation over Rated Speed
289 | P06 Protection | P06.17 | Fault record 1 | P6.31 | Present Fault Record |  |  | P11.04 | First Fault Record
290 | P06 Protection | P06.18 | Fault record 2 | P6.32 | Second Most Recent Fault Record |  |  | P11.05 | Second Most Recent Fault Record
291 | P06 Protection | P06.19 | Fault record 3 | P6.33 | Third Most Recent Fault Record |  |  | P11.06 | Third Most Recent Fault Record
292 | P06 Protection | P06.20 | Fault record 4 | P6.34 | Fourth Most Recent Fault Record |  |  | P11.07 | Fourth Most Recent Fault Record
293 | P06 Protection | P06.21 | Fault record 5 | P6.35 | Fifth Most Recent Fault Record |  |  | P11.08 | Fifth Most Recent Fault Record
294 | P06 Protection | P06.22 | Fault record 6 | P6.36 | Sixth Most Recent Fault Record |  |  | P11.09 | Sixth Most Recent Fault Record
295 | P06 Protection | P06.23 | Fault output option 1 |  |  |  |  | P11.00 | Fault Output Option 1
296 | P06 Protection | P06.24 | Fault output option 2 |  |  |  |  | P11.01 | Fault Output Option 2
297 | P06 Protection | P06.25 | Fault output option 3 |  |  |  |  | P11.02 | Fault Output Option 3
298 | P06 Protection | P06.26 | Fault output option 4 |  |  |  |  | P11.03 | Fault Output Option 4
299 | P06 Protection | P06.27 | Electronic thermal relay selection 2 (motor 2) |  |  |  |  | P06.02 | Electronic Thermal Overload Relay (Motor 2) NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
300 | P06 Protection | P06.28 | Electronic thermal relay action time 2 (motor 2) |  |  |  |  | P06.03 | Electronic Thermal Characteristic (Motor 2)
301 | P06 Protection | P06.29 | PTC detection selection |  |  |  |  | P06.39 | PTC/RTD Detection Selection
302 | P06 Protection | P06.30 | PTC level |  |  |  |  | P06.40 | PTC Level
303 | P06 Protection | P06.31 | Frequency command at malfunction |  |  |  |  | P11.18 | Frequency Command at Fault
304 | P06 Protection | P06.32 | Output frequency at malfunction |  |  |  |  | P11.19 | Output Frequency at Fault
305 | P06 Protection | P06.33 | Output voltage at malfunction |  |  |  |  | P11.20 | Output Voltage at Fault
306 | P06 Protection | P06.34 | DC bus voltage at malfunction |  |  |  |  | P11.21 | DC Bus Voltage at Fault
307 | P06 Protection | P06.35 | Output current at malfunction |  |  |  |  | P11.22 | Output Current at Fault
308 | P06 Protection | P06.36 | IGBT temperature at malfunction |  |  |  |  | P11.23 | IGBT Temperature at Fault
309 | P06 Protection | P06.38 | Motor speed at malfunction |  |  |  |  | P11.25 | RPM of Motor at Fault
310 | P06 Protection | P06.39 | Torque command at malfunction
311 | P06 Protection | P06.40 | Status of the digital input terminal at malfunction |  |  |  |  | P11.26 | Digital Input Status at Fault
312 | P06 Protection | P06.41 | Status of the digital output terminal at malfunction |  |  |  |  | P11.27 | Digital Output Status at Fault
313 | P06 Protection | P06.42 | Drive status at malfunction |  |  |  |  | P11.28 | Drive Status at Fault
314 | P06 Protection | P06.44 | STO latch selection |  |  |  |  | P06.71 | STO Alarm Latch
315 | P06 Protection | P06.45 | Output phase loss detection action (OPHL) |  |  |  |  | P06.45 | Output Phase Loss (OPhL) Detection Selection
316 | P06 Protection | P06.46 | Detection time for output phase loss |  |  |  |  | P06.46 P06.69 | Output Phase Loss Detection time Input Phase Loss Detection Time
317 | P06 Protection | P06.47 | Current detection level for output phase loss |  |  |  |  | P06.47 P06.70 | Output Phase Loss Current Detection Level Input Phase Loss Ripple Detection
318 | P06 Protection | P06.48 | DC brake time for output phase loss |  |  |  |  | P03.51 P06.48 | Brake Delay Time Output Phase Loss DCI Time
319 | P06 Protection | P06.49 | LvX auto-reset
320 | P06 Protection | P06.53 | Input phase loss detection action (OrP) |  |  |  |  | P06.49 | Input Phase Loss Treatment
321 | P06 Protection | P06.55 | Derating protection |  |  |  |  | P06.33 | Drive Derating Method NOTE: THERE ARE INTERDEPENDENCIES BETWEEN P2.10, P6.00/P6.02, P6.33, P6.34. REFER TO PARAMETER DETAILS WHEN SETTING THESE PARAMETERS.
322 | P06 Protection | P06.56 | PT100 voltage level 1 |  |  |  |  | P06.41 | RTD (PT100) Level 1, PTC Level Detection Selection
323 | P06 Protection | P06.57 | PT100 voltage level 2 |  |  |  |  | P06.42 | RTD (PT100) Level 2, PTC Level Detection Selection
324 | P06 Protection | P06.58 | PT100 level 1 frequency protection |  |  |  |  | P06.43 | RTD (PT100) Drop Frequency for PT100 Level 1
325 | P06 Protection | P06.59 | PT100 activation level 1 protection frequency delay time |  |  |  |  | P06.44 | RTD (PT100) Treatment Delay Time
326 | P06 Protection | P06.60 | Software detection GFF current level |  |  |  |  | P06.50 | GFF Detect Current Level (% of INV I-Rated)
327 | P06 Protection | P06.61 | Software detection GFF filter time |  |  |  |  | P06.51 | GFF Low Pass Filter Gain
328 | P06 Protection | P06.63 | Operation time of fault record 1 (Days) |  |  |  |  | P11.10 | Operating Time of Present Fault Record (Day)
329 | P06 Protection | P06.64 | Operation time of fault record 1 (Minutes) |  |  |  |  | P11.11 | Operating Time of Present Fault Record (Minute)
330 | P06 Protection | P06.65 | Operation time of fault record 2 (Days) |  |  |  |  | P11.12 | Operating Time of Second Most Recent Fault Record (Day)
331 | P06 Protection | P06.66 | Operation time of fault record 2 (Minutes) |  |  |  |  | P11.13 | Operating Time of Second Most Recent Fault Record (Minute)
332 | P06 Protection | P06.67 | Operation time of fault record 3 (Days) |  |  |  |  | P11.14 | Operating Time of Third Most Recent Fault Record (Day)
333 | P06 Protection | P06.68 | Operation time of fault record 3 (Minutes) |  |  |  |  | P11.15 | Operating Time of Third Most Recent Fault Record (Minute)
334 | P06 Protection | P06.69 | Operation time of fault record 4 (Days) |  |  |  |  | P11.16 | Operating Time of Fourth Most Recent Fault Record (Day)
335 | P06 Protection | P06.70 | Operation time of fault record 4 (Minutes) |  |  |  |  | P11.17 | Operating Time of Fourth Most Recent Fault Record (Minute)
336 | P06 Protection | P06.71 | Low current setting level |  |  |  |  | P06.52 | Low Current Level
337 | P06 Protection | P06.72 | Low current detection time |  |  |  |  | P06.53 | Low Current Detection Time
338 | P06 Protection | P06.73 | Low current action |  |  |  |  | P06.54 | Low Current Action
339 | P06 Protection | P06.80 | Fire mode |  |  |  |  | P06.55 | Fire Mode
340 | P06 Protection | P06.81 | Operating frequency in fire mode |  |  |  |  | P06.56 | Fire Mode Operation Frequency
341 | P06 Protection | P06.88 | Operation times in fire mode
342 | P06 Protection | P06.90 | Operation time of fault record 5 (days)
343 | P06 Protection | P06.91 | Operation time of fault record 5 (Minutes)
344 | P06 Protection | P06.92 | Operation time of fault record 6 (days)
345 | P06 Protection | P06.93 | Operation time of fault record 6 (Minutes)
346 | P07 Special | P07.00 | Software brake chopper threshold level |  |  | P6.18 | Braking Voltage Level | P06.28 | Dynamic Braking Voltage Level
347 | P07 Special | P07.01 | DC brake current level | P1.18 | DC Injection Current Level | P1.18 | DC Injection Current Level | P01.25 | DC Injection Current Level
348 | P07 Special | P07.02 | DC brake time at start-up | P1.20 | DC Injection during Start-up | P1.20 | DC Injection during Start-up | P01.26 | DC Injection Time During Start-up
349 | P07 Special | P07.03 | DC brake time at STOP | P1.21 | DC Injection during Stopping | P1.21 | DC Injection during Stopping | P01.27 | DC Injection Time During Stopping
350 | P07 Special | P07.04 | DC brake frequency at STOP | P1.22 | Start-point for DC Injection | P1.22 | Start-point for DC Injection | P01.28 | Start-Point for DC Injection During Stopping
351 | P07 Special | P07.05 | Voltage increasing gain
352 | P07 Special | P07.06 | Restart after momentary power loss | P6.02 | Momentary Power Loss | P6.02 | Momentary Power Loss | P06.08 | Momentary Power Loss
353 | P07 Special | P07.07 | Allowed power loss duration | P6.12 | Maximum Allowable Power Loss Time | P6.12 | Maximum Allowable Power Loss Time | P06.22 | Maximum Allowable Power Loss Time
354 | P07 Special | P07.08 | Base Block time | P6.13 | Base-Block Time for Speed Search | P6.13 | Base-Block Time for Speed Search | P06.23 | Base-Block Time for Speed Search
355 | P07 Special | P07.09 | Current limit of speed tracking | P6.14 | Maximum Speed Search Current Level | P6.14 | Maximum Speed Search Current Level | P06.24 | Maximum Speed Search Current Level
356 | P07 Special | P07.10 | Restart after fault action |  |  |  |  | P06.06 | Base Block Speed Search after Fault (oc,ov,bb)
357 | P07 Special | P07.11 | Number of times of restart after fault | P6.01 | Auto Restart after Fault | P6.01 | Auto Restart after Fault | P06.04 | Auto Restart after Fault
358 | P07 Special | P07.12 | Speed tracking during start-up |  |  |  |  | P06.07 | Speed Search at Start
359 | P07 Special | P07.13 | dEb function selection |  |  |  |  | P06.61 | Decel Energy Backup (DEB) Decel Selection
360 | P07 Special | P07.15 | Dwell time at acceleration |  |  |  |  | P06.65 | Dwell Time at Accel
361 | P07 Special | P07.16 | Dwell frequency at acceleration |  |  |  |  | P06.66 | Dwell Frequency at Accel
362 | P07 Special | P07.17 | Dwell time at deceleration |  |  |  |  | P06.67 | Dwell Time at Decel
363 | P07 Special | P07.18 | Dwell frequency at deceleration |  |  |  |  | P06.68 | Dwell Frequency at Decel
364 | P07 Special | P07.19 | Fan cooling control |  |  |  |  | P06.31 | Cooling Fan Control
365 | P07 Special | P07.20 | Emergency stop (EF) & force to stop selection |  |  |  |  | P03.56 | Emergency Stop (EF) & Force Stop Selection
366 | P07 Special | P07.21 | Automatic energy- saving setting |  |  |  |  | P02.23 | Automatic Energy-Saving Operation
367 | P07 Special | P07.22 | Energy-saving gain |  |  |  |  | P02.24 | Power Saving Gain
368 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | P6.04 | Auto Voltage Regulation | P6.04 | Auto Voltage Regulation | P06.10 | Auto Voltage Regulation
369 | P07 Special | P07.24 | Torque command filter time (V/F and SVC control mode) |  |  |  |  | P02.03 | Torque Compensation Filter
370 | P07 Special | P07.25 | Slip compensation filter time (V/F,SVC control mode) |  |  | P2.09 | Slip Comp Time Constant | P02.25 | Slip Compensation Filter
371 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | P2.02 | Auto-torque Boost | P2.02 | Auto-torque Boost | P02.02 | Torque Compensation Gain
372 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | P2.01 | Slip Compensation | P2.01 | Slip Compensation | P02.01 | Slip Compensation Gain
373 | P07 Special | P07.29 | Slip deviation level |  |  |  |  | P02.26 | Slip Deviation Level
374 | P07 Special | P07.30 | Over-slip deviation detection time |  |  |  |  | P02.27 | Slip Deviation Detection time
375 | P07 Special | P07.31 | Over-slip deviation treatment |  |  |  |  | P02.28 | Slip Deviation Treatment
376 | P07 Special | P07.32 | Motor oscillation compensation factor |  |  | P6.37 | Hunting Gain | P02.29 | Hunting Gain
377 | P07 Special | P07.33 | Auto-restart interval of fault |  |  |  |  | P06.05 | Reset Time for Auto Restart after fault
378 | P07 Special | P07.38 | PMSVC voltage feed forward gain
379 | P07 Special | P07.46 | OOB sampling time
380 | P07 Special | P07.47 | Number of OOB sampling times
381 | P07 Special | P07.48 | OOB average sampling angle
382 | P07 Special | P07.62 | dEb gain (Kp)
383 | P07 Special | P07.71 | Torque compensation gain (motor 2)
384 | P07 Special | P07.72 | Slip compensation gain (motor 2)
385 | P07 Special | P07.73 | Torque compensation gain (motor 3)
386 | P07 Special | P07.74 | Slip compensation gain (motor 3)
387 | P07 Special | P07.75 | Torque compensation gain (motor 4)
388 | P07 Special | P07.76 | Slip compensation gain (motor 4)
389 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | P7.00 | Input Terminal for PID Feedback | P7.00 & P7.10 | Input Terminal for PID Feedback | P07.00 | PID Action/Mode
390 | P08 Hi Func PID | P08.01 | Proportional gain (P) | P7.20 | Proportional Control | P7.20 | Proportional Control | P07.13 | Proportional Gain
391 | P08 Hi Func PID | P08.02 | Integral time (I) | P7.21 | Integral Control | P7.21 | Integral Control | P07.14 | Integral Time
392 | P08 Hi Func PID | P08.03 | Differential time (D) | P7.22 | Derivative Control | P7.22 | Derivative Control | P07.15 | Derivative Value
393 | P08 Hi Func PID | P08.04 | Upper limit of integral control | P7.23 | Upper Bound for Integral Control | P7.23 | Upper Bound for Integral Control | P07.16 | Upper Limit for Integral Time
394 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | P7.25 | PID Output Frequency Limit | P7.25 | PID Output Frequency Limit | P07.18 | PID Output Frequency Limit
395 | P08 Hi Func PID | P08.06 | PID feedback value by communication protocol |  |  |  |  | P07.19 | PID Feedback Value
396 | P08 Hi Func PID | P08.07 | PID delay time | P7.24 | Derivative Filter Time Constant | P7.24 | Derivative Filter Time Constant | P07.17 | Derivative Filter Time Constant
397 | P08 Hi Func PID | P08.08 | Feedback signal detection time | P7.26 | Feedback Signal Detection Time | P7.26 | Feedback Signal Detection Time | P07.20 | Feedback Signal Detection Time
398 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | P7.27 | PID Feedback Loss | P7.27 | PID Feedback Loss | P07.21 | PID Feedback Loss
399 | P08 Hi Func PID | P08.10 | Sleep frequency |  |  |  |  | P07.29 | Sleep Reference
400 | P08 Hi Func PID | P08.11 | Wake-up frequency |  |  |  |  | P07.30 | Wake-up Reference
401 | P08 Hi Func PID | P08.12 | Sleep time |  |  |  |  | P07.31 | Sleep Time
402 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | P3.18 | PID Deviation Level | P3.18 | PID Deviation Level | P03.36 | PID Deviation Level
403 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | P3.19 | PID Deviation Time | P3.19 | PID Deviation Time | P03.37 | PID Deviation Time
404 | P08 Hi Func PID | P08.15 | PID feedback signal filter time
405 | P08 Hi Func PID | P08.16 | PID compensation selection |  |  |  |  | P07.24 | PID Offset Selection
406 | P08 Hi Func PID | P08.17 | PID compensation |  |  |  |  | P07.04 | PID Offset Value
407 | P08 Hi Func PID | P08.18 | Sleep mode function setting |  |  |  |  | P07.27 | Source of Sleep
408 | P08 Hi Func PID | P08.19 | Wake-up integral limit |  |  |  |  | P07.28 | Integral Limit During Sleep
409 | P08 Hi Func PID | P08.20 | PID mode selection |  |  |  |  | P07.25 | PID Mode Selection
410 | P08 Hi Func PID | P08.21 | Enable PID to change the operation direction |  |  |  |  | P07.26 | PID Reverse Enable
411 | P08 Hi Func PID | P08.22 | Wake-up delay time |  |  |  |  | P07.32 | Wake-up Delay Time
412 | P08 Hi Func PID | P08.23 | PID control flag
413 | P08 Hi Func PID | P08.26 | PID output command limit (reverse limit)
414 | P08 Hi Func PID | P08.27 | Acceleration / deceleration time for PID command
415 | P08 Hi Func PID | P08.29 | Frequency base corresponding to 100.00% PID
416 | P08 Hi Func PID | P08.31 | Proportional gain 2
417 | P08 Hi Func PID | P08.32 | Integral time 2
418 | P08 Hi Func PID | P08.33 | Differential time 2
419 | P08 Hi Func PID | P08.65 | PID target value source | P7.02 | PID Setpoint Source | P7.02 | PID Setpoint Source | P07.02 | PID Setpoint Source Display (when PID enabled, this parameter data will be mapped from P4.00~P4.01 dependent upon whether in Remote=4.00 or Local=4.01)
420 | P08 Hi Func PID | P08.66 | PID target value setting
421 | P08 Hi Func PID | P08.67 | Master and auxiliary reverse running cutoff frequency
422 | P08 Hi Func PID | P08.68 | PID deviation limit
423 | P08 Hi Func PID | P08.69 | Integral separation level
424 | P08 Hi Func PID | P08.70 | Smart start-up level
425 | P08 Hi Func PID | P08.71 | Smart start-up frequency command
426 | P08 Hi Func PID | P08.72 | Smart start-up acceleration time
427 | P08 Hi Func PID | P08.75 | PID2 parameter switch condition
428 | P08 Hi Func PID | P08.76 | PID2 parameter switch deviation 1
429 | P08 Hi Func PID | P08.77 | PID2 parameter switch deviation 2
430 | P08 Hi Func PID | P08.78 | Allowed reverse running time after start-up
431 | P09 Communication | P09.00 | Communication address | P9.00 | Communication Address | P9.00 | Communication Address | P09.00 | VFD Comm Address
432 | P09 Communication | P09.01 | COM1 transmission speed | P9.01 | Transmission Speed | P9.01 | Transmission Speed | P09.01 | Modbus Baud Rate
433 | P09 Communication | P09.02 | COM1 transmission fault treatment | P9.03 | Transmission Fault Treatment | P9.03 | Transmission Fault Treatment | P09.03 | Modbus Fault Select
434 | P09 Communication | P09.03 | COM1 time-out detection | P9.04 P9.05 | Time Out Detection Time Out Duration | P9.04 P9.05 | Time Out Detection Time Out Duration | P09.04 P09.05 | Modbus Time Out Detection Modbus Time Out Duration
435 | P09 Communication | P09.04 | COM1 communication protocol | P9.02 | Communication Protocol | P9.02 | Communication Protocol | P09.02 | Modbus Protocol
436 | P09 Communication | P09.09 | Communication response delay time | P9.05* | Time Out Duration | P9.05* | Time Out Duration | P09.35 | Response Delay Time
437 | P09 Communication | P09.10 | Communication main frequency
438 | P09 Communication | P09.11 | Block transfer 1 | P9.11 | Block Transfer Parameter 1 |  |  | P09.09 | Block Transfer Data Location 1
439 | P09 Communication | P09.12 | Block transfer 2 | P9.12 | Block Transfer Parameter 2 |  |  | P09.10 | Block Transfer Data Location 2
440 | P09 Communication | P09.13 | Block transfer 3 | P9.13 | Block Transfer Parameter 3 |  |  | P09.11 | Block Transfer Data Location 3
441 | P09 Communication | P09.14 | Block transfer 4 | P9.14 | Block Transfer Parameter 4 |  |  | P09.12 | Block Transfer Data Location 4
442 | P09 Communication | P09.15 | Block transfer 5 | P9.15 | Block Transfer Parameter 5 |  |  | P09.13 | Block Transfer Data Location 5
443 | P09 Communication | P09.16 | Block transfer 6 | P9.16 | Block Transfer Parameter 6 |  |  | P09.14 | Block Transfer Data Location 6
444 | P09 Communication | P09.17 | Block transfer 7 | P9.17 | Block Transfer Parameter 7 |  |  | P09.15 | Block Transfer Data Location 7
445 | P09 Communication | P09.18 | Block transfer 8 | P9.18 | Block Transfer Parameter 8 |  |  | P09.16 | Block Transfer Data Location 8
446 | P09 Communication | P09.19 | Block transfer 9 | P9.19 | Block Transfer Parameter 9 |  |  | P09.17 | Block Transfer Data Location 9
447 | P09 Communication | P09.20 | Block transfer 10 | P9.20 | Block Transfer Parameter 10 |  |  | P09.18 | Block Transfer Data Location 10
448 | P09 Communication | P09.21 | Block transfer 11 | P9.21 | Block Transfer Parameter 11 |  |  | P09.19 | Block Transfer Data Location 11
449 | P09 Communication | P09.22 | Block transfer 12 | P9.22 | Block Transfer Parameter 12 |  |  | P09.20 | Block Transfer Data Location 12
450 | P09 Communication | P09.23 | Block transfer 13 | P9.23 | Block Transfer Parameter 13 |  |  | P09.21 | Block Transfer Data Location 13
451 | P09 Communication | P09.24 | Block transfer 14 | P9.24 | Block Transfer Parameter 14 |  |  | P09.22 | Block Transfer Data Location 14
452 | P09 Communication | P09.25 | Block transfer 15 | P9.25 | Block Transfer Parameter 15 |  |  | P09.23 | Block Transfer Data Location 15
453 | P09 Communication | P09.26 | Block transfer 16 |  |  |  |  | P09.24 | Block Transfer Data Location 16
454 | P09 Communication | P09.30 | Communication decoding method
455 | P09 Communication | P09.33 | PLC command force to 0 |  |  |  |  | P09.85 | PLC Frequency Command Force to 0
456 | P09 Communication | P09.35 | PLC address |  |  |  |  | P09.37 | PLC Address
457 | P09 Communication | P09.60 | Communication card identification |  |  |  |  | P09.44 | Comm Card Type
458 | P09 Communication | P09.61 | Firmware version of communication card |  |  |  |  | P09.45 | Comm Card Version
459 | P09 Communication | P09.62 | Product code |  |  |  |  | P09.46 | Comm Card Production Code
460 | P09 Communication | P09.63 | Error code |  |  |  |  | P09.47 | Comm Card Fault Code
461 | P09 Communication | P09.74 | Set Comm Master Protocol
462 | P09 Communication | P09.75 | Communication card IP configuration (Ethernet) |  |  |  |  | P09.48 | Comm Card IP Configuration
463 | P09 Communication | P09.76 | Communication card IP address 1 (Ethernet) |  |  |  |  | P09.49 | Comm Card IP Address Octet 1
464 | P09 Communication | P09.77 | Communication card IP address 2 (Ethernet) |  |  |  |  | P09.50 | Comm Card IP Address Octet 2
465 | P09 Communication | P09.78 | Communication card IP address 3 (Ethernet) |  |  |  |  | P09.51 | Comm Card IP Address Octet 3
466 | P09 Communication | P09.79 | Communication card IP address 4 (Ethernet) |  |  |  |  | P09.52 | Comm Card IP Address Octet 4
467 | P09 Communication | P09.80 | Communication card address mask 1 (Ethernet) |  |  |  |  | P09.53 | Comm Card Mask Octet 1
468 | P09 Communication | P09.81 | Communication card address mask 2 (Ethernet) |  |  |  |  | P09.54 | Comm Card Mask Octet 2
469 | P09 Communication | P09.82 | Communication card address mask 3 (Ethernet) |  |  |  |  | P09.55 | Comm Card Mask Octet 3
470 | P09 Communication | P09.83 | Communication card address mask 4 (Ethernet) |  |  |  |  | P09.56 | Comm Card Mask Octet 4
471 | P09 Communication | P09.84 | Communication card gateway address 1 (Ethernet) |  |  |  |  | P09.57 | Comm Card Gateway Octet 1
472 | P09 Communication | P09.85 | Communication card gateway address 2 (Ethernet) |  |  |  |  | P09.58 | Comm Card Gateway Octet 2
473 | P09 Communication | P09.86 | Communication card gateway address 3 (Ethernet) |  |  |  |  | P09.59 | Comm Card Gateway Octet 3
474 | P09 Communication | P09.87 | Communication card gateway address 4 (Ethernet) |  |  |  |  | P09.60 | Comm Card Gateway Octet 4
475 | P09 Communication | P09.88 | Communication card password (low word) (Ethernet)
476 | P09 Communication | P09.89 | Communication card password (high word) (Ethernet)
477 | P09 Communication | P09.90 | Reset communication card (Ethernet) |  |  |  |  | P09.63 | Comm Card Factory Reset
478 | P09 Communication | P09.91 | Additional settings for the communication card (Ethernet)
479 | P09 Communication | P09.92 | Communication card status (Ethernet)
480 | P09 Communication | P09.93 | ENETIP Comm Card Fault Select |  |  |  |  | P09.93 | Ethernet Comm Card Fault Select
481 | P09 Communication | P09.94 | ENETIP Comm Card Time Out Detection |  |  |  |  | P09.94 | Ethernet Comm Card Time Out Detection
482 | P09 Communication | P09.95 | ENETIP Comm Card Time Out Duration |  |  |  |  | P09.95 | Ethernet Comm Card Time Out Duration
483 | P10 Spd Fdbk Control | P10.00 | Encoder type selection
484 | P10 Spd Fdbk Control | P10.01 | Encoder pulses per revolution |  |  | P10.00 | Encoder Pulse Per Revolution
485 | P10 Spd Fdbk Control | P10.02 | Encoder input type setting |  |  | P10.01 | Encoder Type
486 | P10 Spd Fdbk Control | P10.04 | Electrical gear at load side A1
487 | P10 Spd Fdbk Control | P10.05 | Electrical gear at motor side B1
488 | P10 Spd Fdbk Control | P10.06 | Electrical gear at load side A2
489 | P10 Spd Fdbk Control | P10.07 | Electrical gear at motor side B2
489 | P10 Spd Fdbk Control | P10.08 | Encoder Loss Action GS30 Only |  |  | P10.05 | Encoder Loss Detection Action
489 | P10 Spd Fdbk Control | P10.09 | Encoder Loss Delay GS30 Only
490 | P10 Spd Fdbk Control | P10.10 | Encoder stall level
491 | P10 Spd Fdbk Control | P10.11 | Detection time of encoder stall
492 | P10 Spd Fdbk Control | P10.12 | Encoder stall action
493 | P10 Spd Fdbk Control | P10.13 | Encoder slip range
494 | P10 Spd Fdbk Control | P10.14 | Detection time of encoder slip
495 | P10 Spd Fdbk Control | P10.15 | Encoder stall and slip error action
496 | P10 Spd Fdbk Control | P10.16 | Pulse input type setting
497 | P10 Spd Fdbk Control | P10.17 | Electrical gear A
498 | P10 Spd Fdbk Control | P10.18 | Electrical gear B
499 | P10 Spd Fdbk Control | P10.21 | PG2 (DI7) pulse input speed command low pass filter time
500 | P10 Spd Fdbk Control | P10.24 | FOC & TQC function control
501 | P10 Spd Fdbk Control | P10.25 | FOC bandwidth for speed observer
502 | P10 Spd Fdbk Control | P10.26 | FOC minimum stator frequency
503 | P10 Spd Fdbk Control | P10.27 | FOC low pass filter time constant
504 | P10 Spd Fdbk Control | P10.28 | FOC gain for excitation current rise time
505 | P10 Spd Fdbk Control | P10.29 | Upper limit of frequency deviation
506 | P10 Spd Fdbk Control | P10.31 | I/F mode, current command
507 | P10 Spd Fdbk Control | P10.32 | PM sensorless speed estimator bandwidth
508 | P10 Spd Fdbk Control | P10.34 | PM sensorless speed estimator low-pass filter gain
509 | P10 Spd Fdbk Control | P10.35 | Active Magnetic Regulator (AMR) (Kp) gain
510 | P10 Spd Fdbk Control | P10.36 | Active Magnetic Regulator (AMR) (Ki) gain
511 | P10 Spd Fdbk Control | P10.39 | Frequency point to switch from I/F mode to PM sensorless mode
512 | P10 Spd Fdbk Control | P10.42 | Initial angle detection pulse value
513 | P10 Spd Fdbk Control | P10.49 | Zero voltage time during start-up
514 | P10 Spd Fdbk Control | P10.51 | Injection frequency
515 | P10 Spd Fdbk Control | P10.52 | Injection magnitude
516 | P10 Spd Fdbk Control | P10.53 | Angle detection method
517 | P11 Advanced | P11.00 | System control
518 | P11 Advanced | P11.01 | Per-unit of system inertia
519 | P11 Advanced | P11.02 | ASR1/ASR2 switch frequency
520 | P11 Advanced | P11.03 | ASR1 low-speed bandwidth
521 | P11 Advanced | P11.04 | ASR2 high-speed bandwidth
522 | P11 Advanced | P11.05 | Zero-speed bandwidth
523 | P11 Advanced | P11.06 | ASR1 (Kp) gain
524 | P11 Advanced | P11.07 | ASR1 (Ki) integral time
525 | P11 Advanced | P11.08 | ASR2 (Kp) gain
526 | P11 Advanced | P11.09 | ASR2 (Ki) integral time
527 | P11 Advanced | P11.10 | ASR Kp gain of zero speed
528 | P11 Advanced | P11.11 | ASR (Ki) integral time of zero speed
529 | P11 Advanced | P11.12 | Gain for ASR speed feed forward
530 | P11 Advanced | P11.13 | PDFF gain value
531 | P11 Advanced | P11.14 | ASR output low pass filter time
532 | P11 Advanced | P11.15 | Notch filter depth
533 | P11 Advanced | P11.16 | Notch filter frequency
534 | P11 Advanced | P11.17 | Forward motor torque limit
535 | P11 Advanced | P11.18 | Forward regenerative torque limit
536 | P11 Advanced | P11.19 | Reverse motor torque limit
537 | P11 Advanced | P11.20 | Reverse regenerative torque limit
538 | P11 Advanced | P11.21 | Flux weakening curve for motor 1 gain value
539 | P11 Advanced | P11.22 | Flux weakening curve for motor 2 gain value
540 | P11 Advanced | P11.23 | Flux weakening area speed response
541 | P11 Advanced | P11.27 | Maximum torque command
542 | P11 Advanced | P11.28 | Torque offset source
543 | P11 Advanced | P11.29 | Torque offset setting
544 | P11 Advanced | P11.30 | High torque offset
545 | P11 Advanced | P11.31 | Middle torque offset
546 | P11 Advanced | P11.32 | Low torque offset
547 | P11 Advanced | P11.33 | Torque command source
548 | P11 Advanced | P11.34 | Torque command
549 | P11 Advanced | P11.35 | Torque command filter time |  |  | P2.03 | Torque Comp Time Constant
550 | P11 Advanced | P11.36 | Speed limit selection
551 | P11 Advanced | P11.37 | Forward speed limit (Torque mode)
552 | P11 Advanced | P11.38 | Reverse speed limit (Torque mode)
553 | P11 Advanced | P11.41 | PWM mode selection
554 | P11 Advanced | P11.42 | System control flag
555 | P13 Macro/User | P13.00 | Industry-specific parameter application | P2.00 | Volts/Hertz Settings | P2.00 | Volts/Hertz Settings | P02.00 | Volts/Hertz Settings
556 | P13 Macro/User | P13.01 | User-defined parameter
557 | P13 Macro/User | P13.02 | User-defined parameter
558 | P13 Macro/User | P13.03 | User-defined parameter
559 | P13 Macro/User | P13.04 | User-defined parameter
560 | P13 Macro/User | P13.05 | User-defined parameter
561 | P13 Macro/User | P13.06 | User-defined parameter
562 | P13 Macro/User | P13.07 | User-defined parameter
563 | P13 Macro/User | P13.08 | User-defined parameter
564 | P13 Macro/User | P13.09 | User-defined parameter
565 | P13 Macro/User | P13.10 | User-defined parameter
566 | P13 Macro/User | P13.11 | User-defined parameter
567 | P13 Macro/User | P13.12 | User-defined parameter
568 | P13 Macro/User | P13.13 | User-defined parameter
569 | P13 Macro/User | P13.14 | User-defined parameter
570 | P13 Macro/User | P13.15 | User-defined parameter
571 | P13 Macro/User | P13.16 | User-defined parameter
572 | P13 Macro/User | P13.17 | User-defined parameter
573 | P13 Macro/User | P13.18 | User-defined parameter
574 | P13 Macro/User | P13.19 | User-defined parameter
575 | P13 Macro/User | P13.20 | User-defined parameter
576 | P13 Macro/User | P13.21 | User-defined parameter
577 | P13 Macro/User | P13.22 | User-defined parameter
578 | P13 Macro/User | P13.23 | User-defined parameter
579 | P13 Macro/User | P13.24 | User-defined parameter
580 | P13 Macro/User | P13.25 | User-defined parameter
581 | P13 Macro/User | P13.26 | User-defined parameter
582 | P13 Macro/User | P13.27 | User-defined parameter
583 | P13 Macro/User | P13.28 | User-defined parameter
584 | P13 Macro/User | P13.29 | User-defined parameter
585 | P13 Macro/User | P13.30 | User-defined parameter
586 | P13 Macro/User | P13.31 | User-defined parameter
587 | P13 Macro/User | P13.32 | User-defined parameter
588 | P13 Macro/User | P13.33 | User-defined parameter
589 | P13 Macro/User | P13.34 | User-defined parameter
590 | P13 Macro/User | P13.35 | User-defined parameter
591 | P13 Macro/User | P13.36 | User-defined parameter
592 | P13 Macro/User | P13.37 | User-defined parameter
593 | P13 Macro/User | P13.38 | User-defined parameter
594 | P13 Macro/User | P13.39 | User-defined parameter
595 | P13 Macro/User | P13.40 | User-defined parameter
596 | P13 Macro/User | P13.41 | User-defined parameter
597 | P13 Macro/User | P13.42 | User-defined parameter
598 | P13 Macro/User | P13.43 | User-defined parameter
599 | P13 Macro/User | P13.44 | User-defined parameter
600 | P13 Macro/User | P13.45 | User-defined parameter
601 | P13 Macro/User | P13.46 | User-defined parameter
602 | P13 Macro/User | P13.47 | User-defined parameter
603 | P13 Macro/User | P13.48 | User-defined parameter
604 | P13 Macro/User | P13.49 | User-defined parameter
605 | P13 Macro/User | P13.50 | User-defined parameter
606 | P14 Protection(2) | P14.50 | Output frequency at malfunction 2
607 | P14 Protection(2) | P14.51 | DC bus voltage at malfunction 2
608 | P14 Protection(2) | P14.52 | Output current at malfunction 2
609 | P14 Protection(2) | P14.53 | IGBT temperature at malfunction 2
610 | P14 Protection(2) | P14.54 | Output frequency at malfunction 3
611 | P14 Protection(2) | P14.55 | DC bus voltage at malfunction 3
612 | P14 Protection(2) | P14.56 | Output current at malfunction 3
613 | P14 Protection(2) | P14.57 | IGBT temperature at malfunction 3
614 | P14 Protection(2) | P14.58 | Output frequency at malfunction 4
615 | P14 Protection(2) | P14.59 | DC bus voltage at malfunction 4
616 | P14 Protection(2) | P14.60 | Output current at malfunction 4
617 | P14 Protection(2) | P14.61 | IGBT temperature at malfunction 4
618 | P14 Protection(2) | P14.62 | Output frequency at malfunction 5
619 | P14 Protection(2) | P14.63 | DC bus voltage at malfunction 5
620 | P14 Protection(2) | P14.64 | Output current at malfunction 5
621 | P14 Protection(2) | P14.65 | IGBT temperature at malfunction 5
622 | P14 Protection(2) | P14.66 | Output frequency at malfunction 6
623 | P14 Protection(2) | P14.67 | DC bus voltage at malfunction 6
624 | P14 Protection(2) | P14.68 | Output current at malfunction 6
625 | P14 Protection(2) | P14.69 | IGBT temperature at malfunction 6
626 | P14 Protection(2) | P14.70 | Fault record 7
627 | P14 Protection(2) | P14.71 | Fault record 8
628 | P14 Protection(2) | P14.72 | Fault record 9
629 | P14 Protection(2) | P14.73 | Fault record 10
630 | P14 Protection(2) | P14.74 | Over-torque detection selection (motor 3)
631 | P14 Protection(2) | P14.75 | Over-torque detection level (motor 3)
632 | P14 Protection(2) | P14.76 | Over-torque detection time (motor 3)
633 | P14 Protection(2) | P14.77 | Over-torque detection selection (motor 4)
634 | P14 Protection(2) | P14.78 | Over-torque detection level (motor 4)
635 | P14 Protection(2) | P14.79 | Over-torque detection time (motor 4)
636 | P14 Protection(2) | P14.80 | Electronic thermal relay selection 3 (motor 3)
637 | P14 Protection(2) | P14.81 | Electronic thermal relay action time 3 (motor 3)
638 | P14 Protection(2) | P14.82 | Electronic thermal relay selection 4 (motor 4)
639 | P14 Protection(2) | P14.83 | Electronic thermal relay action time 4 (motor 4)
640 |  | xN/A |  | P1.09 | Decel 2 to Decel 1 frequency transition | P1.09 | Decel 2 to Decel 1 frequency transition
641 |  | xN/A |  | P1.17 | Skip Frequency Band | P1.17 | Skip Frequency Band
642 |  | xN/A | [5 empty] | P03.10 | Multi-Function Input (DI8)
643 |  | xN/A | [5 empty] | P03.11 | Multi-Function Input (option card DI10 or PLC X12)
644 |  | xN/A | [5 empty] | P03.12 | Multi-Function Input (option card DI11 or PLC X13)
645 |  | xN/A | [5 empty] | P03.13 | Multi-Function Input (option card DI12 or PLC X14)
646 |  | xN/A | [5 empty] | P03.14 | Multi-Function Input (option card DI13 or PLC X15)
647 |  | xN/A | [5 empty] | P03.15 | Multi-Function Input (option card DI14 or PLC X16)
648 |  | xN/A | [5 empty] | P03.16 | Multi-Function Input (option card DI15 or PLC X17)
649 |  | xN/A | [5 empty] | P03.18 | Multi-Function Output Terminal 2 (Relay 2 or PLC Y1)
650 |  | xN/A | [5 empty] | P03.21 | Multi-Function Output Terminal 5 (option card DO10 or RO10, or PLC Y5)
651 |  | xN/A | [5 empty] | P03.22 | Multi-Function Output Terminal 6 (option card DO11 or RO11, or PLC Y6)
652 |  | xN/A | [5 empty] | P03.23 | Multi-Function Output Terminal 7 (option card RO12 or PLC Y7)
653 |  | xN/A | [5 empty] | P03.24 | Multi-Function Output Terminal 8 (option card RO13 or PLC Y10)
654 |  | xN/A | [5 empty] | P03.25 | Multi-Function Output Terminal 9 (option card RO14 or PLC Y11)
655 |  | xN/A | [5 empty] | P03.26 | Multi-Function Output Terminal 10 (option card RO15 or PLC Y12)
656 |  | xN/A | [5 empty] | P03.27 | Multi-Function Virtual Output 11 (DO16, PLC Y13)
657 |  | xN/A | [5 empty] | P03.28 | Multi-Function Virtual Output 12 (DO17, PLC Y14)
658 |  | xN/A | [5 empty] | P03.29 | Multi-Function Virtual Output 13 (DO18, PLC Y15)
659 |  | xN/A | [5 empty] | P03.30 | Multi-Function Virtual Output 14 (DO19, PLC Y16)
660 |  | xN/A | [5 empty] | P03.31 | Multi-Function Virtual Output 15 (DO20, PLC Y17)
661 |  | xN/A |  | P3.17 | Desired Current | P3.17 | Desired Current | P03.52 | Desired Current
662 |  | xN/A | [5 empty] | P03.54 | reserved
663 |  | xN/A | [5 empty] | P03.55 | reserved
664 |  | xN/A | [5 empty] | P03.57 | AUTO to HAND Switching Behavior
675 |  | xN/A | [5 empty] | P04.04 | Analog Input 3 (AI3) Function
676 |  | xN/A | [5 empty] | P04.07 | Trim Reference Frequency
677 |  | xN/A | [5 empty] | P04.08 | Trim Selection
678 |  | xN/A | [5 empty] | P04.14 | reserved
679 |  | xN/A | [5 empty] | P04.19 | AI3 Input Bias (Offset)
680 |  | xN/A | [5 empty] | P04.20 | AI3 Input Bias (Offset) Polarity
681 |  | xN/A | [5 empty] | P04.21 | +AI3 Input Gain
682 |  | xN/A | [5 empty] | P04.22 | -AI3 Input Gain
683 |  | xN/A | [5 empty] | P04.23 | AI3 Filter
684 |  | xN/A | [5 empty] | P04.37 | AI3 Low Voltage Unipolar
685 |  | xN/A | [5 empty] | P04.38 | AI3 Low Hz Percent Unipolar
686 |  | xN/A | [5 empty] | P04.39 | AI3 Mid Voltage Unipolar
687 |  | xN/A | [5 empty] | P04.40 | AI3 Mid Hz Percent Unipolar
688 |  | xN/A | [5 empty] | P04.41 | AI3 High Voltage Unipolar
689 |  | xN/A | [5 empty] | P04.42 | AI3 High Hz Percent Unipolar
690 |  | xN/A | [5 empty] | P04.49 | reserved
691 |  | xN/A | [5 empty] | P04.54 | Analog Output 2 (AO2)
692 |  | xN/A | [5 empty] | P04.55 | AO2 Gain
693 |  | xN/A | [5 empty] | P04.56 | AO2 Negative Value Handle
694 |  | xN/A | [5 empty] | P04.57 | AO2 0~20mA/4~20mA Selection
695 |  | xN/A | [5 empty] | P04.58 | reserved
696 |  | xN/A | [5 empty] | P04.59 | AO2 Offset (Bias)
697 |  | xN/A | [5 empty] | P04.61 | AO2 Output Constant Level
698 |  | xN/A | [5 empty] | P04.63 | Loss of AI1 Signal (4~20mA)
699 |  | xN/A | [5 empty] | P06.32 | PWM Fan Speed
700 |  | xN/A | [5 empty] | P06.57 | Fire Mode Enable Bypass
701 |  | xN/A | [5 empty] | P06.58 | Fire Mode Bypass Delay Time
702 |  | xN/A | [5 empty] | P06.59 | Fire Mode Auto Restart Counter
703 |  | xN/A | [5 empty] | P06.60 | Fire Mode Auto Restart Counter Reset Time
704 |  | xN/A | [5 empty] | P06.62 | DEB Offset Level
705 |  | xN/A | [5 empty] | P06.63 | DEB Disable Voltage Level
706 |  | xN/A | [5 empty] | P06.64 | DEB Delay Time
707 |  | xN/A | [5 empty] | P07.01 | reserved
708 |  | xN/A | [5 empty] | P07.03 | PID Feedback Gain
709 |  | xN/A |  | P7.10 | Keypad PID Setpoint | P7.10 | Keypad PID Setpoint | P07.05 | Keypad PID Setpoint
710 |  | xN/A | Use PLC function with inputs | P7.11 | PID Multi-setpoint 1 | P7.11 | PID Multi-setpoint 1 | P07.06 | PID Multi-Setpoint 1
711 |  | xN/A | Use PLC function with inputs | P7.12 | PID Multi-setpoint 2 | P7.12 | PID Multi-setpoint 2 | P07.07 | PID Multi-Setpoint 2
712 |  | xN/A | Use PLC function with inputs | P7.13 | PID Multi-setpoint 3 | P7.13 | PID Multi-setpoint 3 | P07.08 | PID Multi-Setpoint 3
713 |  | xN/A | Use PLC function with inputs | P7.14 | PID Multi-setpoint 4 | P7.14 | PID Multi-setpoint 4 | P07.09 | PID Multi-Setpoint 4
714 |  | xN/A | Use PLC function with inputs | P7.15 | PID Multi-setpoint 5 | P7.15 | PID Multi-setpoint 5 | P07.10 | PID Multi-Setpoint 5
715 |  | xN/A | Use PLC function with inputs | P7.16 | PID Multi-setpoint 6 | P7.16 | PID Multi-setpoint 6 | P07.11 | PID Multi-Setpoint 6
716 |  | xN/A | Use PLC function with inputs | P7.17 | PID Multi-setpoint 7 | P7.17 | PID Multi-setpoint 7 | P07.12 | PID Multi-Setpoint 7
717 |  | xN/A | [5 empty] | P07.22 | PID Feedback Loss Speed Level Default
718 |  | xN/A | [5 empty] | P07.23 | reserved
719 |  | xN/A | [5 empty] | P08.08 | Power On Counter
720 |  | xN/A | [5 empty] | P08.09 | Power On Day
721 |  | xN/A | [5 empty] | P08.10 | Power On Minute
722 |  | xN/A | [5 empty] | P08.13 | Keypad Communication Fault Treatment
723 |  | xN/A | [5 empty] | P08.14 | Keypad Time Out
724 |  | xN/A | [5 empty] | P08.15 | reserved
725 |  | xN/A | [5 empty] | P08.16 | reserved
726 |  | xN/A | [5 empty] | P08.17 | reserved
727 |  | xN/A | [5 empty] | P08.18 | reserved
728 |  | xN/A | [5 empty] | P08.19 | reserved
729 |  | xN/A | [5 empty] | P09.06 | Parameter Copy
730 |  | xN/A | [5 empty] | P09.25 | reserved
731 |  | xN/A | Use 2000, 2001, 2002 words | P9.26 | Serial Comm Speed Reference | P9.26 | Serial Comm Speed Reference | P09.26 | RS485 Speed Reference
732 |  | xN/A | Use 2000, 2001, 2002 words | P9.27 | Serial Comm RUN Command | P9.27 | Serial Comm RUN Command | P09.27 | RS485 RUN Command
733 |  | xN/A | Use 2000, 2001, 2002 words | P9.28 | Serial Comm Direction Command | P9.28 | Serial Comm Direction Command | P09.28 | RS485 Direction Command
734 |  | xN/A | Use 2000, 2001, 2002 words | P9.29 | Serial Comm External Fault | P9.29 | Serial Comm External Fault | P09.29 | RS485 External Fault
735 |  | xN/A | Use 2000, 2001, 2002 words | P9.30 | Serial Comm Fault Reset | P9.30 | Serial Comm Fault Reset | P09.30 | RS485 Fault Reset
736 |  | xN/A | Use 2000, 2001, 2002 words | P9.31 | Serial Comm JOG Command | P9.31 | Serial Comm JOG Command | P09.31 | RS485 JOG Command
737 |  | xN/A | [5 empty] | P09.32 | reserved
738 |  | xN/A | [5 empty] | P09.36 | reserved
739 |  | xN/A | [5 empty] | P09.38 | Firmware Date Code
740 |  | xN/A | [5 empty] | P09.40 | reserved
741 |  | xN/A | TBD | P9.41 | GS Series Number | P9.41 | GS Series Number | P09.41 | GS Series Number
742 |  | xN/A | [5 empty] | P09.43 | Ignore Comm Card Warning
743 |  | xN/A | [5 empty] | P09.61 | reserved
744 |  | xN/A | [5 empty] | P09.62 | reserved
745 |  | xN/A | [5 empty] | P09.64 | Comm Card External Set
746 |  | xN/A | [5 empty] | P09.65 | reserved
747 |  | xN/A | [5 empty] | P09.66 | reserved
748 |  | xN/A | [5 empty] | P09.67 | reserved
749 |  | xN/A | [5 empty] | P09.68 | reserved
750 |  | xN/A | [5 empty] | P09.69 | Block Transfer Address Pointer 1
751 |  | xN/A | [5 empty] | P09.70 | Block Transfer Address Pointer 2
752 |  | xN/A | [5 empty] | P09.71 | Block Transfer Address Pointer 3
753 |  | xN/A | [5 empty] | P09.72 | Block Transfer Address Pointer 4
754 |  | xN/A | [5 empty] | P09.73 | Block Transfer Address Pointer 5
755 |  | xN/A | [5 empty] | P09.74 | Block Transfer Address Pointer 6
756 |  | xN/A | [5 empty] | P09.75 | Block Transfer Address Pointer 7
757 |  | xN/A | [5 empty] | P09.76 | Block Transfer Address Pointer 8
758 |  | xN/A | [5 empty] | P09.77 | Block Transfer Address Pointer 9
759 |  | xN/A | [5 empty] | P09.78 | Block Transfer Address Pointer 10
760 |  | xN/A | [5 empty] | P09.79 | Block Transfer Address Pointer 11
761 |  | xN/A | [5 empty] | P09.80 | Block Transfer Address Pointer 12
762 |  | xN/A | [5 empty] | P09.81 | Block Transfer Address Pointer 13
763 |  | xN/A | [5 empty] | P09.82 | Block Transfer Address Pointer 14
764 |  | xN/A | [5 empty] | P09.83 | Block Transfer Address Pointer 15
765 |  | xN/A | [5 empty] | P09.84 | Block Transfer Address Pointer 16
766 |  | xN/A | [5 empty] | P09.86 | COMM1 Protocol (via RS-485)
767 |  | xN/A | [5 empty] | P09.87 | BACnet Address
768 |  | xN/A | [5 empty] | P09.88 | BACnet Baud Rate
769 |  | xN/A | [5 empty] | P09.89 | BACnet Device Instance Low Word
770 |  | xN/A | [5 empty] | P09.90 | BACnet Device Instance High Byte
771 |  | xN/A | [5 empty] | P09.91 | BACnet Max Polling Address
772 |  | xN/A | [5 empty] | P09.92 | BACnet Password
773 |  | xN/A | [5 empty] | P09.96 | reserved
774 |  | xN/A | [5 empty] | P09.97 | reserved
775 |  | xN/A | [5 empty] | P09.98 | reserved
776 |  | xN/A | [5 empty] | P09.99 | reserved
777 |  | xN/A | [5 empty] | P10.00 | Circulative Control
778 |  | xN/A | [5 empty] | P10.01 | Number of Connected Motors
779 |  | xN/A | [5 empty] | P10.02 | Desired Run Time of Each Motor in Minutes
780 |  | xN/A | [5 empty] | P10.03 | Motor Switch Delay Time During Increasing Demand
781 |  | xN/A | [5 empty] | P10.04 | Motor Switch Delay Time During Decreasing Demand
782 |  | xN/A | [5 empty] | P10.05 | Aux Motor Switch Delay Time During Fix Amount Circulation in Seconds
783 |  | xN/A | [5 empty] | P10.06 | Aux Motor Switch Frequency During Fix Amount Circulation in Hz
784 |  | xN/A | [5 empty] | P10.07 | Circulative Control Malfunction Action
785 |  | xN/A | [5 empty] | P10.08 | AUX Motor Stop Frequency
786 |  | xN/A | [5 empty] | P11.24 | HeatSink Temperature at Fault
787

## Crossref GS3 to GS30
GS3 Parameter Summary |  |  |  |  | GS30 Parameter Summary
GS3 Parameter Group | GS3 Parameter | Description | Range | Default | Parameter Group | Parameter No. | Parameter Description | Range | Range (con't) | R/W | Default | Key Difference to Note from GS3 | SEE DISCLAIMER
P00 Motor | P0.00 | Motor Nameplate Voltage | 230V: 200/208/220/230/240 460V: 380/400/415/440/460/480 | 240 480 | P01 Basic | P01.02 | Motor 1, Rated Voltage (Nameplate) | 230V models: 0.0-255.0 V 460V models: 0.0-510.0 V |  | R/W | 220.0 440.0
P00 Motor | P0.01 | Motor Nameplate Amps | Drive Rated Amps X .3 to 1.0 | Drive Rated Amps x 1.0 | P05 Motor | P05.01 | Induction Motor 1, Full-load amps | 10-120% of the drive's rated current |  | R/W | Model dependent
P00 Motor | P0.02 | Motor Base Frequency | 50/60/400 | 60 | P01 Basic | P01.01 | Motor 1 Fbase | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00 | 0.00–599.00 Hz
P00 Motor | P0.03 | Motor Base RPM | 375 to 9999 RPM | 1750 | P05 Motor | P05.03 | Induction Motor 1, Rated speed (rpm) | 0-xxxxx rpm (Depending on the motor's number of poles) 1710 (60Hz, 4 poles); 1410 (50Hz, 4 poles) |  | ♦R/W | 1710
P00 Motor | P0.04 | Motor Maximum RPM | P0.03 to 9999 RPM | P0.03 | P01 Basic | P01.00 | Maximum operation frequency | 0.00-599.00 Hz |  | R/W | 60.00 / 50.00 | GS30 set max hertz as drive limit, not RPM.
P00 Motor | P0.05 | Auto detection |  |  | P05 Motor | P05.00 | Motor parameter auto-tuning
P00 Motor | P0.06 | Rotor resistance |  |  | P05 Motor | P05.06 | Induction Motor 1, Stator resistance (Rs)
P00 Motor | P0.07 | No Load Amps |  |  | P05 Motor | P05.05 | Induction Motor 1, No-load amps
P01 Ramps | P1.00 | Stop Methods | 00: Ramp to Stop 01: Coast to Stop | 0 | P00 Drive | P00.22 | Stop method | 0: Ramp to stop 1: Coast to stop |  | ♦R/W | 0
P01 Ramps | P1.01 | Acceleration Time 1 | 0.1 to 600.0 sec | 10 | P01 Basic | P01.12 | Acceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
P01 Ramps | P1.02 | Deceleration Time 1 | 0.1 to 600.0 sec | 30 | P01 Basic | P01.13 | Deceleration time 1 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
P01 Ramps | P1.03 | Accel S-curve | 0 to 7 | 0 | P01 Basic | P01.24 | S-curve for acceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
P01 Ramps | P1.03 |  |  |  | P01 Basic | P01.25 | S-curve for acceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
P01 Ramps | P1.04 | Decel S-curve | 0 to 7 | 0 | P01 Basic | P01.26 | S-curve for deceleration begin time 1 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
P01 Ramps | P1.04 |  |  |  | P01 Basic | P01.27 | S-curve for deceleration arrival time 2 | P01.45 = 0: 0.00-25.00 sec. P01.45 = 1: 0.0-250.0 sec. |  | ♦R/W | 0.20 0.2 | 0.00–25.00 sec.
P01 Ramps | P1.05 | Acceleration Time 2 | 0.1 to 600.0 sec | 10 | P01 Basic | P01.14 | Acceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
P01 Ramps | P1.06 | Deceleration Time 2 | 0.1 to 600.0 sec | 30 | P01 Basic | P01.15 | Deceleration time 2 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0
P01 Ramps | P1.07 | Select method to use 2nd Accel/Decel | 00: RMP2 from DI terminal 01: Transition Frequencies P1.08 & P1.09 | 0 | P02 Digital IO | P02.06* P02.03 - P02.07 | Multifunction Inputs Command for P02.03 - P02.07 |  |  |  |  | Choose any Dix input with Function 8-1st and 2nd acceleration / deceleration time selection
P01 Ramps | P1.08 | Accel 1 to Accel 2 frequency transition | 0.0 to 400.0 Hz | 0 | P01 Basic | P01.23 | TRANS ACC/DEC1-4 Switch frequency between first and fourth Accel./Decel. | 0.00-599.00 Hz |  | ♦R/W | 0 | Set 3 parameters..P01.18,19 and 23. Switch Frequency between First and Fourth Accel./Decel. Must use 4th accel settings, not 2nd.
P01 Ramps | P1.08 |  |  |  | P01 Basic | P01.18 | Acceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0 | *external terminal has priority over this parameter
P01 Ramps | P1.08 |  |  |  | P01 Basic | P01.19 | Deceleration time 4 | P01.45 = 0: 0.00-600.00 sec. P01.45 = 1: 0.0-6000.0 sec. |  | ♦R/W | 10.00 10.0 | * accel and decel must be at same frequency and configured between 1st and 4th accel/decel only. No equivalent P01.09 parameter
P01 Ramps | P1.09 | Decel 2 to Decel 1 frequency transition | 0.0 to 400.0 Hz | 0 |  | NA
P01 Ramps | P1.10 | Skip Frequency 1 | 0.0 to 400.0 Hz | 0 | P01 Basic | P01.28 | Skip frequency 1 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
P01 Ramps | P1.10 |  |  |  | P01 Basic | P01.29 | Skip frequency 1 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
P01 Ramps | P1.11 | Skip Frequency 2 | 0.0 to 400.0 Hz | 0 | P01 Basic | P01.30 | Skip frequency 2 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
P01 Ramps | P1.11 |  |  |  | P01 Basic | P01.31 | Skip frequency 2 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
P01 Ramps | P1.12 | Skip Frequency 3 | 0.0 to 400.0 Hz | 0 | P01 Basic | P01.32 | Skip frequency 3 (upper limit) | 0.00-599.00 Hz |  | R/W | 0 | 0.00–599.00 Hz- Use Upper and lower setting
[5 empty] | P01 Basic | P01.33 | Skip frequency 3 (lower limit) | 0.00-599.00 Hz |  | R/W | 0
P01 Ramps | P1.13 | Skip Freq 4 |  |  |  | NA
P01 Ramps | P1.14 | Skip Freq 5 |  |  |  | NA
P01 Ramps | P1.17 | Skip Frequency Band | 0.0 to 20.0 Hz | 0 |  | NA
P01 Ramps | P1.18 | DC Injection Current Level | 00 to 100 % | 0 | P07 Special | P07.01 | DC brake current level | 0-100% |  | ♦R/W | 0
P01 Ramps | P1.20 | DC Injection during Start-up | 0.0 to 5.0 sec | 0 | P07 Special | P07.02 | DC brake time at start-up | 0.0-60.0 sec. |  | ♦R/W | 0 | 0.0–60.0 sec.
P01 Ramps | P1.21 | DC Injection during Stopping | 0.0 to 25.0 sec | 0 | P07 Special | P07.03 | DC brake time at STOP | 0.0-60.0 sec. |  | ♦R/W | 0 | 0.0–60.0 sec.
P01 Ramps | P1.22 | Start-point for DC Injection | 0.0 to 60.0 Hz | 0 | P07 Special | P07.04 | DC brake frequency at STOP | 0.00-599.00 Hz |  | ♦R/W | 0
P02 V/Hz | P2.00 | Volts/Hertz Settings |  | 0 | P00 Drive | P00.11 | Speed (Velocity) Control mode | 0: IMVF (V/F control) 1: IMVFPG (V/F control + encoder) 2: IM/PM SVC (IM or PM space vector control) 5: IMFOC Sensorless (field-oriented sensorless vector control) Note: For option 2 (SVC), see P05.33 for induction motor (IM) or permanent magnent (PM) motor selection. |  | R/W | 0 | For Control mode: First, Ensure V/F Mode is selected
P02 V/Hz | P2.00 | Volts/Hertz Settings | 00: General Purpose 01: High Starting Torque 02: Fans and Pumps 03: Custom | 0 | P01 Basic | P01.43 | V/F curve selection | 0: V/F curve determined by P01.00-P01.08 1: V/F curve to the power of 1.5 2: V/F curve to the power of 2 |  | R/W | 0 | Second, Select the curve, or
P02 V/Hz | P2.00 | Volts/Hertz Settings |  | 0 | P13 Macro/User | P13.00 | Industry-specific parameter application | 00: Disabled 01: User-defined parameter 02: Compressor 03: Fan 04: Pump 05: Conveyor 06: Machine tool 07: Packing 08: Textiles 10: Logistics 11: Tension PID 12: Tension PID + master / auxiliary frequency |  | R/W | 0 | Third, choose the Industry specific application setting
P02 V/Hz | P2.01 | Slip Compensation | 0.0 to 10.0 | 0 | P07 Special | P07.27 | Slip compensation gain (V/F and SVC control mode) | 0.00-10.00 |  | ♦R/W | 0.00 (Default value is 1.00 in SVC mode)
P02 V/Hz | P2.02 | Auto-torque Boost | 00 to 10 | 0 | P07 Special | P07.26 | Torque compensation gain (V/F and SVC control mode) | IM: 0-10 (when P05.33 = 0) PM: 0-5000 (when P05.33 = 1 or 2) |  | ♦R/W | 1
P02 V/Hz | P2.03 | Torque Comp Time Constant | 00 to 10 | 0.05 | P07 Special | P07.24 | Torque Command Filter Time (V/F and SVC Control Mode) | 0.001 to 10.000 seconds |  |  | 0.05
P02 V/Hz | P2.04 | Mid-point Frequency | 0.1 to 400 Hz | 1.5 | P01 Basic | P01.03 | Motor 1, Mid-point frequency 1 | 0.00-599.00 Hz |  | R/W | 3
P02 V/Hz | P2.05 | Mid-point Voltage | 115V/230V: 2.0 to 255V 460V: 2.0 to 510V 575V: 2.0 to 637V | 10.0 20.0 24.0 | P01 Basic | P01.04 | Motor 1, Mid-point voltage 1 | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V |  | ♦R/W | 11.0 22.0
P02 V/Hz | P2.06 | Min. Output Frequency | 0.1 to 20.0 Hz | 1.5 | P01 Basic | P01.07 | Motor 1, Minimum output frequency | 0.00-599.00 Hz |  | R/W | 0.5
P02 V/Hz | P2.07 | Min. Output Voltage | 115V/230V: 2.0 to 50.0V 460V: 2.0 to 100.0V 575V: 2.0 to 130.6V | 10.0 20.0 24.0 | P01 Basic | P01.08 | Motor 1, Minimum output voltage | 120V / 230V models: 0.0-240.0 V 460V models: 0.0-480.0 V |  | ♦R/W | 1.0 2.0
P02 V/Hz | P2.08 | PWM Carrier Frequency | 115V/230V/460V; 01 to 15 kHz 575V; 01 to 10 kHz | 12 6 | P00 Drive | P00.17 | Carrier frequency | Variable Torque: 2-15 kHz Constant Torque: 2-15 kHz Note: When P00-11=5 (IMFOC Sensorless), the maximum setting value for the carrier frequency is 10 kHz. |  | R/W | 4
P02 V/Hz | P2.09 | Slip Time Constant |  |  |  | NA
P02 V/Hz | P2.10 | Control Mode |  |  |  | NA
P03 Digital | P3.00 | Source of Operation Command | 00: Operation determined by digital keypad 01: Operation determined by external control terminals, keypad STOP is enabled 02: Operation determined by external control terminals, keypad STOP is disabled 03: Operation determined by RS-485 interface, keypad STOP is enabled 04: Operation determined by RS-485 interface, keypad STOP is disabled | 0 | P00 Drive | P00.21 P00.31 | Operation command source (AUTO, REMOTE) | 0: Digital keypad 1: External terminals 2: RS-485 communication input 3: Not used 5: Communication card Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function settings 41/42 or 56 or with GS4-KPD (optional) |  | R/W | 0
P03 Digital | P3.00 |  |  |  | P00 Drive | P00.32 | Digital keypad STOP function | 0: STOP key disabled 1: STOP key enabled |  | ♦R/W | 0
P03 Digital | P3.01 | Multi-function Input Terminals (DI1 - DI2) | 00: DI1 - FWD / STOP, DI2 - REV / STOP 01: DI1 - RUN / STOP, DI2- REV / FWD 02: DI1 - RUN momentary (N.O.) DI2 - REV / FWD DI3 - STOP momentary (N.C.) | 0 | P02 Digital IO | P02.00 | Two-wire / three wire operation control | 0: No function 1: Two-wire mode 1, power on for operation control (DI1: FWD/STOP, DI2: REV/STOP) 2: Two-wire mode 2, power on for operation control (DI1: RUN/STOP, DI2: REV/FWD) 3: Three-wire, power on for operation control (DI1: RUN, DI2: REV/FWD, DI3: STOP) 4: Two-wire mode 1, Quick Start (DI1: FWD/STOP, DI2: REV/STOP) 5: Two-wire mode 2, Quick Start (DI1: RUN/STOP, DI2: REV/FWD) 6: Three-wire, Quick Start (DI1: RUN, DI2: REV/FWD, DI3: STOP) | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0
P03 Digital |  |  |  |  | P02 Digital IO | P02.01 | Multi-function input command 1 (FWD/DI1) | 0: No function 1: Multi-step speed command 1 / multi-step position command 1 2: Multi-step speed command 2 / multi-step position command 2 3: Multi-step speed command 3 / multi-step position command 3 4: Multi-step speed command 4 / multi-step position command 4 5: Reset 6: JOG [by external control or GS4- KPD (optional)] 7: Acceleration / deceleration speed inhibit 8: 1st and 2nd acceleration / deceleration time selection 9: 3rd and 4th acceleration / deceleration time selection 10: External Fault (EF) Input (P07.20) 11: Base Block (B.B.) input from external source 12: Output stop 13: Cancel the setting of auto- acceleration / auto-deceleration time 15: Rotating speed command from AI1 16: Rotating speed command from AI2 18: Force to stop (P07.20) 19: Digital up command 20: Digital down command 21: PID function disabled 22: Clear the counter 23: Input the counter value (DI6) 24: FWD JOG command 25: REV JOG command 26: TQC / Field Oriented Control (FOC) mode selection 27: ASR1 / ASR2 selection 28: Emergency stop (EF1) 29: Signal confirmation for Y-connection 30: Signal confirmation for ti. -connection 31: High torque bias (P11.30) 32: Middle torque bias (P11.31) 33: Low torque bias (P11.32) 38: Disable writing EEPROM function 39: Torque command direction 40: Force coasting to stop 41: HAND switch 42: AUTO switch 48: Mechanical gear ratio switch 49: Enable drive | 50: Slave dEb action to execute 51: Selection for PLC mode bit 0 52: Selection for PLC mode bit 1 56: Local / Remote selection 58: Enable fire mode (with RUN command) 59: Enable fire mode (without RUN command) 70: Force auxiliary frequency return to 0 71: Disable PID function, force PID output return to 0 72: Disable PID function, retain the output value before disabled 73: Force PID integral gain return to 0, disable integral 74: Reverse PID feedback 81: Simple positioning zero point position signal input 82: OOB loading balance detection 83: Multi-motor (IM) selection bit 0 84: Multi-motor (IM) selection bit 1 | R/W | 0 | 0-94 only use if P02.00 = 0
P03 Digital |  |  |  |  | P02 Digital IO | P02.02 | Multi-function input command 2 (REV/DI2) | See P02.01 for values. |  | R/W | 0 | 0-94 only use if P02.00 = 0
P03 Digital | P3.02 | Multi-function Input (DI3) | 00: External Fault (N.O.) 01: External Fault (N.C.) 02: External Reset 03: Multi-Speed/PID SP Bit 1 04: Multi-Speed/PID SP Bit 2 05: Multi-Speed/PID SP Bit 3 06: Reserved 07: Reserved 08: Reserved 09: Jog 10: External Base Block (N.O.) 11: External Base Block (N.C.) 12: Second Accel/Decel Time 13: Speed Hold 14: Increase Speed 15: Decrease Speed 16: Reset Speed to Zero 17: PID Disable (N.O.) 18: PID Disable (N.C.) 99: Input Disable | 0 | P02 Digital IO | P02.03 | Multi-function input command 3 (DI3) | See P02.01 for values. |  | R/W | 1 | 0-94
P03 Digital | P3.03 | Multi-function Input (DI4) |  | 3 | P02 Digital IO | P02.04 | Multi-function input command 4 (DI4) | See P02.01 for values. |  | R/W | 2 | 0-94
P03 Digital | P3.04 | Multi-function Input (DI5) |  | 4 | P02 Digital IO | P02.05 | Multi-function input command 5 (DI5) | See P02.01 for values. |  | R/W | 3 | 0-94
P03 Digital | P3.05 | Multi-function Input (DI6) |  | 5 | P02 Digital IO | P02.06 | Multi-function input command 6 (DI6) | See P02.01 for values. |  | R/W | 4 | 0-94
P03 Digital | P3.06 | DI7 |  |  | P02 Digital IO | P02.07 | Multi-function input command 7 (DI7) | See P02.01 for values. |  | R/W | 0 | 0-94
P03 Digital | P3.06 | DI8 |  |  | P02 Digital IO | P02.26 | Multi-function input command 10 (DI10) Available with optional IO Card | See P02.01 for values. |  |  | 0 | 0-94
P03 Digital | P3.08 | DI9 |  |  | P02 Digital IO | P02.27 | Multi-function input command 11 (DI11) Available with optional IO Card | See P02.01 for values. |  |  | 0 | 0-94
P03 Digital | P3.09 | DI10 |  |  | P02 Digital IO | P02.28 | Multi-function input command 12 (DI12) Available with optional IO Card | See P02.01 for values. |  |  | 0 | 0-94
P03 Digital | P3.10 | DI11 |  |  |  | NA
P03 Digital | P3.11 | Multi-Function Output Terminal 1 | 00: AC Drive Running 01: AC Drive Fault 02: At Speed 03: Zero Speed 04: Above Desired Frequency 05: Below Desired Frequency 06: At Maximum Speed 07: Over torque detected 08: Above Desired Current 09: Below Desired Current 10: PID Deviation Alarm | 0 | P02 Digital IO | P02.13 P02.16 | Multi-function output 1 (R1) Multi-function output 1 (DO1) | 0: No function 1: Indication during RUN 2: Operation speed reached 3: Desired frequency reached 1 (P02.22) 4: Desired frequency reached 2 (P02.24) 5: Zero speed (Frequency command) 6: Zero speed including STOP (Frequency command) 7: Over-torque 1 (P06.06-06.08) 8: Over-torque 2 (P06.09-06.11) 9: Drive is ready 10: Low voltage warning (Lv) (P06.00) 11: Malfunction indication 13: Overheat warning (P06.15) 14: Software brake signal indicator (P07.00) 15: PID feedback error (P08.13, P08.14) 16: Slip error (oSL) 17: Count value reached, does not return to 0 (P02.20) 18: Count value reached, return to 0 (P02.19) 19: External interrupt B.B. input (Base Block) 20: Warning output 21: Over-voltage 22: Over-current stall prevention 23: Over-voltage stall prevention 24: Operation mode 25: Forward command 26: Reverse command 29: Output when frequency � P02.34 30: Output when frequency < P02.34 31: Y-connection for the motor coil 32: t.-connection for the motor coil 33: Zero speed (actual output frequency) 34: Zero speed including STOP (actual output frequency) 35: Error output selection 1 (P06.23) 36: Error output selection 2 (P06.24) 37: Error output selection 3 (P06.25) 38: Error output selection 4 (P06.26) 40: Speed reached (including STOP) 42: Crane function 43: Motor speed detection 44: Low current output (use with P06.71-06.73) 45: UVW output electromagnetic valve switch 46: Master dEb output | 51: Analog output control for RS-485 interface 52: Output control for communication cards 53: Fire mode indication 66: SO output logic A 67: Analog input level reached 68: SO output logic B 73: Over-torque 3 74: Over-torque 4 75: Forward RUN status 76: Reverse RUN status | ♦R/W | 11 0 | 0-76 Relay Output 0-76; Multi-function output 1 (DO1)- Transisitor output, not relay output..ensure adequante current for field device
P03 Digital | P3.12 | Multi-Function Output Terminal 2 | same as P3.11 | 1 | P02 Digital IO | P02.17 | Multi-function output 2(DO2) | See P02.16 for values. |  | ♦R/W | 0 | 0-76; Multi-function output 2 (DO2)- Transisitor output, not relay output..ensure adequante current for field device
P03 Digital | P3.13 | DO 3 |  |  | P02 Digital IO | P02.36 | Multi-function output 10(DO10) Available with optional IO Card | See P02.16 for values. |  | ♦R/W | 0
P03 Digital | P3.14 | DO 4 |  |  | P02 Digital IO | P02.37 | Multi-function output 11(DO11) Available with optional IO Card | See P02.16 for values. |  | ♦R/W | 0
[5 empty] | P02 Digital IO | P02.38 | Multi-function output 12(DO12) Available with optional IO Card | See P02.16 for values. |  | ♦R/W | 0
P03 Digital | P3.16 | Desired Frequency | 0.0 to 400.0 Hz | 0 | P02 Digital IO | P02.22 | Desired frequency reached 1 | 0.00-599.00 Hz |  | ♦R/W | 60.00 / 50.00
P03 Digital | P3.17 | Desired Current | 0.0 to <Drive Rated Amps> | 0 |  | NA
P03 Digital | P3.18 | PID Deviation Level | 1.0 to 50.0 % | 10 | P08 Hi Func PID | P08.13 | PID feedback signal error deviation level | 1.0-50.0% |  | ♦R/W | 10
P03 Digital | P3.19 | PID Deviation Time | 0.1 to 300.0 sec | 5 | P08 Hi Func PID | P08.14 | PID feedback signal error deviation detection time | 0.1-300.0 sec. |  | ♦R/W | 5
P03 Digital | P3.20 | Desired Freq 2 |  |  |  | NA
P03 Digital | P3.31 | 2nd Source of Operation Command |  |  |  | NA
P04 Analog | P4.00 | Source of Frequency Command | 00: Frequency determined by keypad potentiometer 01: Frequency determined by digital keypad up/down 02: Frequency determined by 0 to +10V input on AI terminal with jumpers 03: Frequency determined by 4 to 20mA input on AI terminal with jumpers 04: Frequency determined by 0 to 20mA input on AI terminal with jumpers 05: Frequency determined by RS-232C/ RS-485 communication interface | 0 | P00 Drive | P00.20 | Master frequency command source (AUTO, REMOTE) | 0: Digital keypad 1: RS-485 communication input 2: External analog input (Refer to P03.00) 3: External UP / DOWN terminal (digital input terminals) 4: Pulse input (DI7) without direction command (refer to P10.16 for pulse input config) 6: Not used 7: Digital keypad VR/potentiometer dial (GS20 only) 8: Communication card 9: PID controller Note: HOA (Hand-Off-Auto) function is valid only when you use with digital input (DI) function setting 41/42 or 56 or with GS4-KPD (optional). |  | ♦R/W | 0 | 0-9
P04 Analog | P4.00 |  |  |  | P03 Analog IO | P03.01 | Analog input selection (AI2) |  |  | ♦R/W | 0 | 0-21
P04 Analog | P4.01 | Analog Input Offset Polarity | 00: No Offset 01: Positive Offset 02: Negative Offset | 0 | P03 Analog IO | P03.08 | Positive / negative bias mode (AI2) | 0: No bias 1: Lower than or equal to bias 2: Greater than or equal to bias 3: The absolute value of the bias voltage while serving as the center 4: Bias serves as the center |  | ♦R/W | 0 | 4 different mode in GS30
P04 Analog | P4.02 | Analog Input Offset | 0.0 to 100.0% | 0 | P03 Analog IO | P03.04 | Analog input bias (AI2) | -100.0-100.0% |  | ♦R/W | 0 | -100 - 100%, calcs work differently in GS30
P04 Analog | P4.03 | Analog Input Gain | 0.0 to 300.0% | 100 | P03 Analog IO | P03.12 | Analog input gain (AI2) | -500.0-500.0% |  | ♦R/W | 100 | -500 - 500%, calcs work differentin in GS30
P04 Analog | P4.04 | Analog Input Reverse Motion Enable | 00: Forward Motion Only 01: Reverse Motion Enable | 0 | P03 Analog IO | P03.10 | Reverse setting when analog signal input is negative frequency | 0: Negative frequency input is not allowed. The digital keypad or external terminal controls the forward and reverse direction. 1: Negative frequency input is allowed. Positive frequency = run in a forward direction; negative frequency = run in a reverse direction. The digital keypad or external terminal control cannot change the running direction. |  | ♦R/W | 0
P04 Analog | P4.05 | Loss of ACI Signal (4-20mA) | 00: Decelerate to 0Hz 01: Stop immediately and display error code “EF” 02: Continue operation by the last frequency command | 0 | P03 Analog IO | P03.19 | Signal loss selection for analog input 4-20 mA | 0: Disable 1: Continue operation at the last frequency 2: Decelerate to 0 Hz 3: Stop immediately and display "ACE" |  | ♦R/W | 0 | 0-3
P04 Analog | P4.11 | Analog Output Signal | 00: frequency Hz 01: Current A 02: PV | 0 | P03 Analog IO | P03.20 | Multi-function output (A01) | 0: Output frequency (Hz) 1: Frequency command (Hz) 2: Motor speed (Hz) 3: Output current (rms) 4: Output voltage 5: DC bus voltage 6: Power factor 7: Power 8: Output torque 9: AI1 10: AI2 12: Iq current command 13: Iq feedback value 14: Id current command 15: Id feedback value 16: Vq-axis voltage command 17: Vd-axis voltage command 18: Torque command 19: PG2 (DI7) frequency command 21: RS-485 analog output 22: Communication card analog output 23: Constant voltage output |  | ♦R/W | 0
P04 Analog | P4.12 | Analog Output Gain | 00 to 200% | 100 | P03 Analog IO | P03.21 | Analog output gain (A01) | 0.0-500.0% |  | ♦R/W | 100 | 0-500%
P04 Analog | P4.13 | 2nd Source of Freq Command |  |  |  | NA
P04 Analog | P4.14 | 2nd Source of Freq Command Offset Polarity |  |  |  | NA
P04 Analog | P4.15 | 2nd Source of Freq Command Offset |  |  |  | NA
P04 Analog | P4.16 | 2nd Source of Freq Command Gain |  |  |  | NA
P04 Analog | P4.17 | Trim Reference Frequency |  |  |  | NA
P04 Analog | P4.18 | Trim Mode Select |  |  |  | NA
P05 Presets | P5.00 | Jog | 0.0 to 400.0 Hz | 6 | P01 Basic | P01.22 | JOG frequency | 0.00-599.00 Hz |  | ♦R/W | 6 | 0.00–599.00 Hz
P05 Presets | P5.01 | Multi-Speed 1 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.00 | 1st step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.02 | Multi-Speed 2 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.01 | 2nd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.03 | Multi-Speed 3 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.02 | 3rd step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.04 | Multi-Speed 4 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.03 | 4th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.05 | Multi-Speed 5 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.04 | 5th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.06 | Multi-Speed 6 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.05 | 6th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.07 | Multi-Speed 7 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.06 | 7th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.08 | Multi-Speed 8 | 0.0 to 400.0 Hz | 6 | P04 Multi Step Spd | P04.07 | 8th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 6 | 0.00–599.00 Hz
P05 Presets | P5.09 | Multi-Speed 9 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.08 | 9th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.10 | Multi-Speed 10 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.09 | 10th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.11 | Multi-Speed 11 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.10 | 11th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.12 | Multi-Speed 12 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.11 | 12th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.13 | Multi-Speed 13 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.12 | 13th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.14 | Multi-Speed 14 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.13 | 14th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P05 Presets | P5.15 | Multi-Speed 15 | 0.0 to 400.0 Hz | 0 | P04 Multi Step Spd | P04.14 | 15th step speed frequency | 0.00-599.00 Hz |  | ♦R/W | 0 | 0.00–599.00 Hz
P06 Protection | P6.00 | Electronic Thermal Overload Relay | 00: Constant Torque 01: Variable Torque 02: Inactive | 0 | P06 Protection | P06.13 | Electronic thermal relay selection 1 (motor 1) | 0: Inverter motor (with external forced cooling) 1: Standard motor (motor with fan on the shaft) 2: Disabled |  | ♦R/W | 2
P06 Protection | P6.01 | Auto Restart after Fault | 00 to 10 | 0 | P07 Special | P07.11 | Number of times of restart after fault | 0-10 |  | ♦R/W | 0
P06 Protection | P6.02 | Momentary Power Loss | 00: Stop operation after momentary power loss 01: Continue operation after momentary power loss, speed search from Speed Reference 02: Continue operation after momentary power loss, speed search from Minimum Speed | 0 | P07 Special | P07.06 | Restart after momentary power loss | 0: Stop operation 1: Speed tracking by the speed before the power loss 2: Speed tracking by the minimum output frequency |  | ♦R/W | 0
P06 Protection | P6.03 | Reverse Operation Inhibit | 00: Enable Reverse Operation 01: Disable Reverse Operation | 0 | P00 Drive | P00.23 | Motor direction control | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward |  | ♦R/W | 0 | 0: Enable forward / reverse 1: Disable reverse 2: Disable forward
P06 Protection | P6.04 | Auto Voltage Regulation | 00: AVR enabled 01: AVR disabled 02: AVR disabled during decel 03: AVR disabled during stop | 0 | P07 Special | P07.23 | Automatic voltage regulation (AVR) function | 0: Enable AVR 1: Disable AVR 2: Disable AVR during deceleration |  | ♦R/W | 0
P06 Protection | P6.05 | Over-Voltage Stall Prevention | 00: Enable Over-voltage Stall Prevention 01: Disable Over-voltage Stall Prevention | 0 | P06 Protection | P06.01 | Over-voltage stall prevention | 230V models: 0.0-450.0 VDC 460V models: 0.0-900.0 VDC |  | ♦R/W | 380.0 760.0
P06 Protection | P6.06 | Auto Adjustable Accel/Decel | 00: Linear Accel/Decel 01: Auto Accel, Linear Decel 02: Linear Accel, Auto Decel 03: Auto Accel/Decel 04: Auto Accel/Decel Stall Prevention (limited by P1.01, P1.02, P1.05, P1.06) | 0 | P01 Basic | P01.44 | Auto-acceleration and auto-deceleration setting | 0: Linear acceleration and deceleration 1: Auto-acceleration and linear deceleration 2: Linear acceleration and auto- deceleration 3: Auto-acceleration and auto- deceleration 4: Stall prevention by auto- acceleration and auto-deceleration (limited by P01.12 -P01.21) |  | ♦R/W | 0
P06 Protection | P6.07 | Over-Torque Detection Mode | 00: Disabled 01: Enabled during constant speed operation 02: Enabled during acceleration | 0 | P06 Protection | P06.06 | Over-torque detection selection (motor 1) | 0: No function 1: Continue operation after over-torque detection during constant speed operation 2: Stop after over-torque detection during constant speed operation 3: Continue operation after over-torque detection during RUN 4: Stop after over-torque detection during RUN 5. Sys Acc/Dec time |  | ♦R/W | 0 | 0-5
P06 Protection | P6.08 | Over-Torque Detection Level | 30 to 200% | 150 | P06 Protection | P06.07 | Over-torque detection level (motor 1) | 10-250% (100% corresponds to the rated current of the drive) |  | ♦R/W | 120 | 10-250% (100% corresponds to the rated current of the drive)
P06 Protection | P6.09 | Over-Torque Detection Time | 0.1 to 10.0 | 0.1 | P06 Protection | P06.08 | Over-torque detection time (motor 1) | 0.1-60.0 sec. |  | ♦R/W | 0.1 | 0.1-60.0 sec.
P06 Protection | P6.10 | Over-Current Stall Prevention during Acceleration | 20 to 200% | 150 | P06 Protection | P06.03 | Over-current stall prevention during acceleration (OCA) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180 | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive)
P06 Protection | P6.11 | Over-Current Stall Prevention during Operation | 20 to 200% | 150 | P06 Protection | P06.04 | Over-current stall prevention during operation (OCN) | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive) |  | ♦R/W | 180 | VT: 0-150% (100% corresponds to the rated current of the drive) CT: 0-200% (100% corresponds to the rated current of the drive)
P06 Protection | P6.12 | Maximum Allowable Power Loss Time | 0.3 to 5.0 sec | 2 | P07 Special | P07.07 | Allowed power loss duration | 0.0-20.0 sec. |  | ♦R/W | 2 | 0.0-20.0 sec.
P06 Protection | P6.13 | Base-Block Time for Speed Search | 0.3 to 5.0 sec | 0.5 | P07 Special | P07.08 | Base Block time | 0.0-60.0 sec. |  | ♦R/W | 0.5 | 0.0-60.0 sec.
P06 Protection | P6.14 | Maximum Speed Search Current Level | 30 to 200% | 150 | P07 Special | P07.09 | Current limit of speed tracking | 20-200% |  | ♦R/W | 100 | 20-200%
P06 Protection | P6.15 | Upper Bound of Output Frequency | 0.1 to 400Hz | 400 | P01 Basic | P01.10 | Output frequency upper limit | 0.00-599.00 Hz |  | ♦R/W | 599
P06 Protection | P6.16 | Lower Bound of Output Frequency | 0.0 to 400Hz | 0 | P01 Basic | P01.11 | Output frequency lower limit | 0.00-599.00 Hz |  | ♦R/W | 0
P06 Protection | P6.17 | Over Voltage Stall Prevention Level | 230V Series - 330.0V to 450.0V 460V Series - 600.0V to 900.0V | 230V series = 390.0V 460V series = 780.0V | P06 Protection | P06.01 | Over Voltage Stall Prevention Level | 0: Disabled 230V 0.0 to 450.0 460V 0.0 to 900 |  |  | 0 380V 760V
P06 Protection | P6.30 | Line Start Lockout | 00: Enable Line Start Lockout 01: Disable Line Start Lockout | 0 | P02 Digital IO | P02.35 | External operation control selection after fault reset and reboot | 0: Lockout 1: Run on Run Command |  | ♦R/W | 0
P06 Protection | P6.31 | Present Fault Record | 00: No Fault occurred 01: Over-current (oc) 02: Over-voltage (ov) 03: Overheat (oH) 04: Overload (oL) 05: Overload 1 (oL1) 06: Overload 2 (oL2) 07: External Fault (EF) 08: CPU failure 1 (CF1) 09: CPU failure 2 (CF2) 10: CPU failure 3 (CF3) 11: Hardware Protection Failure (HPF) 12: Over-current during accel (OCA) 13: Over-current during decel (OCd) 14: Over-current during steady state (OCn) 15:Ground fault or fuse failure (GFF) 16: Reserved 17: Input power 3-phase loss 18: External Base-Block (bb) 19: Auto Adjust accel/decel failure (cFA) 20: Software protection code (codE) | 0 | P06 Protection | P06.17 | Fault record 1 | 0: No fault record 1: Over-current during acceleration (ocA) 2: Over-current during deceleration (ocd) 3: Over-current during steady operation (ocn) 4: Ground fault (GFF) 6: Over-current at stop (ocS) 7: Over-voltage during acceleration (ovA) 8: Over-voltage during deceleration (ovd) 9: Over-voltage during constant speed (ovn) 10: Over-voltage at stop (ovS) 11: Low-voltage during acceleration (LvA) 12: Low-voltage during deceleration (Lvd) 13: Low-voltage during constant speed (Lvn) 14: Low-voltage at stop (LvS) 15: Phase loss protection (orP) 16: IGBT overheating (oH1) 18: IGBT temperature detection failure (tH1o) 21: Over load (oL) 22: Electronic thermal relay 1 protection (EoL1) 23: Electronic thermal relay 2 protection (EoL2) 24: Motor PTC overheating (oH3) 26: Over torque 1 (ot1) 27: Over torque 2 (ot2) 28: Under current (uC) 31: EEPROM read error (cF2) 33: U-phase error (cd1) 34: V-phase error (cd2) 35: W-phase error (cd3) 36: cc (current clamp) hardware error (Hd0) 37: oc (over-current) hardware error (Hd1) 40: Auto-tuning error (AUE) 41: PID loss AI2 (AFE) 43: PG feedback loss (PGF2) 48: AI2 loss (ACE) 49: External fault (EF) 50: Emergency stop (EF1) 51: External Base Block (bb) 52: Password is locked (Pcod) 54: Illegal command (CE1) 55: Illegal data address (CE2) 56: Illegal data value (CE3) 57: Data is written to read-only address (CE4) 58: Modbus transmission time-out (CE10) | 61: Y-connection / fl-connection switch error (ydc) 62: Deceleration energy backup error (dEb) 63: Over slip error (oSL) 72: STO Loss (STL1) 76: STO (STo) 77: STO Loss 2 (STL2) 78: STO Loss 3 (STL3) 79: U-phase Over-current before run (Aoc) 80: V-phase Over-current before run (boc) 81: W-phase Over-current before run (coc) 82: Output phase loss U phase (oPL1) 83: Output phase loss V phase (oPL2) 84: Output phase loss W phase (oPL3) 87: Low frequency overload protection (oL3) 89: Rotor position detection error (roPd) 111: InrCOM time-out error (ictE) 121: Internal communication error (CP20) 123: Internal communication error (CP22) 124: Internal communication error (CP30) 126: Internal communication error (CP32) 127: Internal communication error (CP33) 128: Over-torque 3 (ot3) 129: Over-torque 4 (ot4) 134: Internal communication error (EoL3) 135: Internal communication error (EoL4) 140: Oc hardware error (Hd6) 141: GFF occurs before run (b4GFF) 142: Auto-tune error 1 (DC test stage) (AuE1) 143: Auto-tune error 2 (High frequency test stage) (AuE2) 144: Auto-tune error 3 (Rotary test stage) (AuE3) | R/W | 0 | 0-149
P07 PID | P7.00 | Input Terminal for PID Feedback | 00: Inhibit PID operation 01: Forward-acting (heating loop) PID feedback, PV from AVI (0 to + 10V 02: Forward-acting (heating loop) PID feedback, PV from ACI (4 to 20mA) 03: Reverse-acting (cooling loop) PID feedback, PV from AVI (0 to +10V). 04: Reverse-acting (cooling loop) PID feedback, PV from ACI (4 to 20mA). | 0 | P08 Hi Func PID | P08.00 | Terminal selection of PID feedback | 0: No function 1: Negative PID feedback: by analog input (P03.00, P03.01) 2: Negative PID feedback: by single- phase input (DI7), without direction (P10.16=5) 4: Positive PID feedback: by analog input (P03.00, P03.01) 5: Positive PID feedback: by single- phase input (DI7), without direction (P10.16=5) 7: Negative PID feedback: by communication protocols 8: Positive PID feedback: by communication protocols |  | ♦R/W | 0 | 0-8
P07 PID | P7.01 | PV 100% Value | 0.0 to 999 | 100 |  | xN/A
P07 PID | P7.02 | PID Setpoint Source | 00: Keypad 01: Serial Communications | 0 | P08 Hi Func PID | P08.65 | PID target value source | 0: Frequency command (P00.20, P00.30) 1: P08.66 2: RS-485 communication input 3: External analog input (refer to P03.00, P03.01) 6: Communication card |  | ♦R/W | 0 | 0-6
P07 PID | P7.03 | PID Feedback Gain |  |  |  | NA
P07 PID | P7.04 | PID Setpoint Offset Polarity |  |  |  | NA
P07 PID | P7.05 | PID Setpoint Offset |  |  |  | NA
P07 PID | P7.06 | PID Setpoint Gain |  |  |  | NA
P07 PID | P7.10 | Keypad PID Setpoint | 0.0 to 999 | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2001H (see Parameter details)
P07 PID | P7.11 | PID Multi-setpoint 1 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.12 | PID Multi-setpoint 2 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.13 | PID Multi-setpoint 3 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.14 | PID Multi-setpoint 4 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.15 | PID Multi-setpoint 5 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.16 | PID Multi-setpoint 6 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.17 | PID Multi-setpoint 7 | 0.0 to 999 | 0 |  | NA
P07 PID | P7.20 | Proportional Control | 0.0 to 10.0 | 1 | P08 Hi Func PID | P08.01 | Proportional gain (P) | 0.0-1000.0 (When P08.23 bit 1=0) 0.00-100.00 (When P08.23 bit 1=1) |  | ♦R/W | 1
P07 PID | P7.21 | Integral Control | 0.00 to 100.0 sec | 1 | P08 Hi Func PID | P08.02 | Integral time (I) | 0.00-100.00 sec. |  | ♦R/W | 1
P07 PID | P7.22 | Derivative Control | 0.00 to 1.00 sec | 0 | P08 Hi Func PID | P08.03 | Differential time (D) | 0.00-1.00 sec. |  | ♦R/W | 0
P07 PID | P7.23 | Upper Bound for Integral Control | 00 to 100% | 100 | P08 Hi Func PID | P08.04 | Upper limit of integral control | 0.0-100.0% |  | ♦R/W | 100
P07 PID | P7.24 | Derivative Filter Time Constant | 0.0 to 2.5 sec | 0 | P08 Hi Func PID | P08.07 | PID delay time | 0.0-2.5 sec. |  | ♦R/W | 0
P07 PID | P7.25 | PID Output Frequency Limit | 00 to 110% | 100 | P08 Hi Func PID | P08.05 | PID output command limit (positive limit) | 0.0-110.0% |  | ♦R/W | 100
P07 PID | P7.26 | Feedback Signal Detection Time | 0.0 to 3600 sec. | 60 | P08 Hi Func PID | P08.08 | Feedback signal detection time | 0.0-3600.0 sec. |  | ♦R/W | 0
P07 PID | P7.27 | PID Feedback Loss | 00: Warn and AC Drive Stop 01: Warn and Continue Operation | 0 | P08 Hi Func PID | P08.09 | Feedback signal fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: Warn and operate at last frequency |  | ♦R/W | 0 | 0-3
P07 PID | P7.28 | PID Feedback Loss Preset Speed |  |  |  | NA
P08 Display | P8.00 | User Defined Display Function | 00: Output Frequency (Hz) 01: Motor Speed (RPM) 02: Output Freq. X P8.01 03: Output Current (A) 04: Motor Output Current (%) 05: Output Voltage (V) 06: DC Bus Voltage (V) 07: PID Setpoint 08: PID Feedback Signal (PV) 09: Frequency Setpoint | 0 | P00 Drive | P00.04 | User Display | 0: Output Amps (A) (unit: Amp) 1: Counter Value (c) (unit: CNT) 2: Output Frequency (H.) (unit: Hz) 3: DC Bus Voltage (V) (unit: VDC) 4: Output Voltage (E) (unit: VAC) 5: Power Factor (n) (unit: deg) 6: Output Power (P) (unit: kW) 7: Calculated RPM (r) (unit: rpm) 8: Est Output Torque (t) (unit: %) 10: PID Feedback (b) (unit: %) 11: AI1 Analog Input Signal (1.) (unit: %) 12: AI2 Analog Input Signal (2.) (unit: %) 14: IGBT Temperature (i.) (unit: 0C) 16: DI Input Status (ON / OFF) (i) 17: DO Output Status (ON / OFF) (o) 18: Multi-Speed Step (S) 19: CPU DI Input Status (d) 20: CPU DO Output Status (0.) 22: Pulse input frequency (S.) 25: Overload count (0.00-100.00%) (o.) (unit: %) 26: Ground fault GFF (G.) (unit: %) 27: DC bus voltage ripple (r.) (unit: VDC) 28: Display PLC register D1043 data (C) 30: Display the output of User-defined (U) 31: Display P00-05 user gain (K) 35: Control mode display 36: Present operating carrier frequency of the drive (J.) (Unit: Hz) 38: Display the drive status (6.) 39: Display the drive's estimated output torque, positive and negative, using N•m as unit (t 0.0: positive torque; -0.0: negative torque) (C.) 40: Torque command (L.) (unit: %) 41: kWh display (J) (unit: kWh) 42: PID target value (h.) (unit: %) 43: PID compensation (o.) (unit: %) 44: PID output frequency (b.) (unit: Hz) 46: Auxiliary frequency value (U.) (unit: Hz) 47: Master frequency value (A) (unit: Hz) 48: Frequency value after addition and subtraction of master and auxiliary frequency (L.) (unit: Hz) 51: PMSVC torque offset 58: P00.05 User gain display (K) (Does not display decimal places.) 62: I2t (o.) (unit: %) 63: Error code (E.) 64: Warning code (n.) 65: Accumulated motor operation record (day) (r.) (refer to P05.32) |  | ♦R/W | 3 | 0-60
P08 Display | P8.01 | Frequency Scale Factor | 0.01 to 160.0 | 1 | P00 Drive | P00.05 | Coefficient Gain in Actual Output Frequency Display (H Page scale) | 0.00-160.00 |  | ♦R/W | 1
P08 Display | P8.02 | Backlight Timer |  |  |  | NA
P09 Communication | P9.00 | Communication Address | 01 to 254 | 1 | P09 Communication | P09.00 | Communication address | 1-254 |  | ♦R/W | 1
P09 Communication | P9.01 | Transmission Speed | 00: 4800 baud 01: 9600 baud 02: 19200 baud 03: 38400 baud | 1 | P09 Communication | P09.01 | COM1 transmission speed | 4.8-115.2 Kbps |  | ♦R/W | 9.6 | 4.8-115.2 Kbps
P09 Communication | P9.02 | Communication Protocol | 00: Modbus ASCII mode 7 data bits,no parity,2 stop bits 01: Modbus ASCII mode 7 data bits,even parity,1 stop bit 02: Modbus ASCII mode 7 data bits,odd parity,1 stop bit 03: Modbus RTU mode 8 data bits,no parity,2 stop bits 04: Modbus RTU mode 8 data bits,even parity,1 stop bit 05: Modbus RTU mode 8 data bits,odd parity,1 stop bit | 0 | P09 Communication | P09.04 | COM1 communication protocol | 1: 7, N, 2 (ASCII) 2: 7, E, 1 (ASCII) 3: 7, O, 1 (ASCII) 4: 7, E, 2 (ASCII) 5: 7, O, 2 (ASCII) 6: 8, N, 1 (ASCII) 7: 8, N, 2 (ASCII) 8: 8, E, 1 (ASCII) 9: 8, O, 1 (ASCII) 10: 8, E, 2 (ASCII) 11: 8, O, 2 (ASCII) 12: 8, N, 1 (RTU) 13: 8, N, 2 (RTU) 14: 8, E, 1 (RTU) 15: 8, O, 1 (RTU) 16: 8, E, 2 (RTU) 17: 8, O, 2 (RTU) |  | ♦R/W | 1
P09 Communication | P9.03 | Transmission Fault Treatment | 00: Display fault and continue operating 01: Display fault and RAMP to stop 02: Display fault and COAST to stop 03: No fault displayed and continue operating | 0 | P09 Communication | P09.02 | COM1 transmission fault treatment | 0: Warn and continue operation 1: Fault and ramp to stop 2: Fault and coast to stop 3: No warning, no fault, and continue operation |  | ♦R/W | 3
P09 Communication | P9.04 | Time Out Detection | 00: Disable 01: Enable | 0 | P09 Communication | P09.03 | COM1 time-out detection | 0.0-100.0 sec. |  | ♦R/W | 0 | 0.0-100.0 sec.
P09 Communication | P9.05 | Time Out Duration | 0.1 to 60.0 seconds | 0.5 | P09 Communication | P09.09 | Communication response delay time | 0.0-200.0 ms |  | ♦R/W | 2 | 0.0-200.0 ms
P09 Communication | P9.07 | Parameter Lock | 00: All parameters can be set and read 01: All parameters are read-only | 0 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
P09 Communication | P9.08 | Restore to Default | 99: Restores all parameters to factory defaults | 0 | P00 Drive | P00.02 | Restore to Default | 0: No function 1: Parameter Lock 2: Convert to GS2 mode (Step 1 of 2) 3: Not used 4: Not used 5: Reset kWh Display to 0 6: Reset PLC 8: Disable Keypad Run 9: Reset all parameters to 50Hz defaults 10: Reset all parameters to 60Hz defaults 11: Reset all parameters to 50Hz defaults (retain user-defined parameter values P13.01~P13.50) 12: Reset all parameters to 60Hz defaults (retain user-defined parameter values P13.01~P13.50) 13: Not used 20: Convert to GS2 mode (Step 2 of 2) |  | R/W | 0
P09 Communication | P9.26 | Serial Comm Speed Reference | 0.0 to 400.0 Hz | 60 |  | xN/A | Use internal PLC or external comms to write to Word 2001H (see Parameter details)
P09 Communication | P9.27 | Serial Comm RUN Command | 00: Stop 01: Run | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2000H (see Parameter details)
P09 Communication | P9.28 | Serial Comm Direction Command | 00: Forward 01: Reverse | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2000H (see Parameter details)
P09 Communication | P9.29 | Serial Comm External Fault | 00: No fault 01: External fault | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2100H (see Parameter details)
P09 Communication | P9.30 | Serial Comm Fault Reset | 00: No action 01: Fault Reset | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2002H (see Parameter details)
P09 Communication | P9.31 | Serial Comm JOG Command | 00: Stop 01: Jog | 0 |  | xN/A | Use internal PLC or external comms to write to Word 2000H (see Parameter details)
P09 Communication | P9.39 | Firmware Version | #.## | #.## | P00 Drive | P00.06 | Firmware version | Read only |  | Read | ~
P09 Communication | P9.40 | Param Copy |  |  |  | NA
P09 Communication | P9.41 | GS Series Number | 01: GS1 02: GS2 03: GS3 | ## | P00 Drive | P00.00 | GS30 Model ID- Identity Code
P09 Communication | P9.42 | Manufacturer Model Information | 00: GS2-20P5 (230V 1ph/3ph 0.5hp) 01: GS2-21P0 (230V 1ph/3ph 1hp) 02: GS2-22P0 (230V 1ph/3ph 2hp) 03: GS2-23P0 (230V 1ph/3ph 3hp) 04: GS2-25P0 (230V 3ph 5hp) 05: GS2-27P5 (230V 3ph 7.5hp) 06: Reserved 07: GS2-41P0 (460V 3ph 1hp) 08: GS2-42P0 (460V 3ph 2hp) 09: GS2-43P0 (460V 3ph 3hp) 10: GS2-45P0 (460V 3ph 5hp) 11: GS2-47P5 (460V 3ph 7.5hp) 12: GS2-4010 (460V 3ph 10hp) 13: GS2-10P2 (115V 1ph 0.25hp) 14: GS2-10P5 (115V 1ph 0.5hp) 15: GS2-11P0 (115V 1ph 1hp) 16~20: Reserved 21: GS2-51P0 (575V 3ph 1hp) 22: GS2-52P0 (575V 3ph 2hp) 23: GS2-53P0 (575V 3ph 3hp) 24: GS2-55P0 (575V 3ph 5hp) 25: GS2-57P5 (575V 3ph 7.5hp) 26: GS2-5010 (575V 3ph 10hp) | ## | [5 empty] | Read
P10 Encoder | P10.00 | Encoder PPR |  |  | P09 Communication | P10.01 | Encoder pulses per revolution | 0-65535 |  | ♦R/W | 0
P10 Encoder | P10.01 | Encoder Type |  |  | P09 Communication | P10.02 | Encoder input type setting | 0-65535 |  | ♦R/W | 0
P10 Encoder | P10.02 | Encoder Proportional Control |  |  | P09 Communication | NA |  | 0-65535 |  | ♦R/W | 0
P10 Encoder | P10.03 | Encoder Integral Control |  |  | P09 Communication | NA |  | 0-65535 |  | ♦R/W | 0
P10 Encoder | P10.04 | Encoder Speed Control Output Limit |  |  | P09 Communication | NA |  | 0-65535 |  | ♦R/W | 0
P10 Encoder | P10.05 | Encoder Loss Detection |  |  | P09 Communication | P10.08 | Encoder Loss Action GS30 Only | 0-65535 |  | ♦R/W | 0