## Blank
[15 empty] | Related Parameters |  |  | PID Parameters
[14 empty] | Factory Reset: |  |  | P08.00 | PID FBK SEL | 1
[14 empty] | P00.02 | Reset Drive Params | 10 | P08.01 | P Gain of PID | 1
[17 empty] | P08.02 | I Gain of PID | 1
[14 empty] | Motor: |  |  | P08.03 | D Gain of PID | 0
[11 empty] | P08.26 | 100 | Output Scaling | P05.01 | Motor1: FLA |  | P08.04 | Up Limit for I | 100
P08.65 | 0 | SP Source | [8 empty] | P08.21 | 0 | Direction Limit | P05.02 | Motor1: Power |  | P08.05 | PID Out-Limit % | 100
[14 empty] | P05.03 | Rated Speed (rpm) |  | P08.06 | PID Fbk Value | 0
[14 empty] | P05.04 | Motor1: Poles |  | P08.07 | PID Out-Filter | 0
[17 empty] | P08.P08 | FBK Detect Time | 0
[5 empty] | P08.01 (P) | 1 | P | [6 empty] | Drive: |  |  | P08.09 | PID FBK Loss | 0
[5 empty] | P08.02 (I) | 1 | I | [6 empty] | P00.20 | REMOTE Freq Source (PID) | 0 | P08.10 | Sleep Point | 0
Motor: |  |  |  |  | P08.03 (D) | 0 | D |  |  |  | P08.00 | 1 | PV Source & FWD/REV Acting | P00.21 | REMOTE Run/Stop Source (DI) |  | P08.11 | Wake Point | 0
P05.01 |  | Motor1: FLA | [11 empty] | P00.29 | LOC/REM Operation | 4 | P08.12 | Sleep Time | 0
P05.02 |  | Motor1: Power | [11 empty] | P00.30 | LOCAL Freq Source (POT) |  | P08.13 | PID DEV. Level | 10
p05.03 |  | Rated Speed (rpm) |  |  | P08.04 | 100 | Intergral Limit | [6 empty] | P00.31 | LOCAL Run/Stop Source (DI) | 0 | P08.14 | PID DEV. Time | 5
P05.04 |  | Motor1: Poles |  |  | P08.20 | 0 | PID Mode |  |  |  | PV Conditioning (using AI1): |  |  | P01.00 | Motor1: Max Freq (Hz) | 60 | P08.15 | PID FBK Filter | 5
[5 empty] | P08.23 | 2 | PID Ctrl |  |  |  | P03.00 |  | AI1 = PV | P01.07 | Motor1: Min Freq (Hz) |  | P08.16 | PID Offset Way | 0
Drive Control: | [10 empty] | P03.03 | 0 | AI1 Offset (%) | P01.12 | Acceleration (Sec) |  | P08.17 | PID Offset | 0
P00.20 | 0 | REMOTE Freq Source (PID) | [8 empty] | P03.11 | 100 | AI1 Gain (%) | P01.13 | Decel (Sec) |  | P08.18 | Source of Sleep | 0
P00.21 |  | REMOTE Run/Stop Source (DI) | [8 empty] | P03.15 |  | AI1 Filter (Sec) | P02.00 | DI1:RUN/STOP, DI2:FWD/REV |  | P08.19 | I Limit for Wake | 50
P00.29 | 4 | LOC/REM Operation | [11 empty] | P02.03 | DI3: LOC/REM |  | P08.20 | PID Mode | 0
P00.30 |  | LOCAL Freq Source (POT) | [8 empty] | Display: |  |  | P02.04 | DI4: Auto/Man |  | P08.21 | Direction Limit | 0
P00.31 | 0 | LOCAL Run/Stop Source (DI) | [8 empty] | P00.04 |  | User Display: PV (%) |  |  |  | P08.22 | Wake Delay Time | 0
P01.00 | 60 | Motor1: Max Freq (Hz) | [11 empty] | Display: |  |  | P08.23 | PID CTRL BIT | 2
P01.07 |  | Motor1: Min Freq (Hz) | [11 empty] | P00.04 | User Display |  | P08.26 | PID Neg.OutLmit% | 100
P01.12 |  | Acceleration (Sec) |  |  | Color Code: | [11 empty] | P08.27 | PID Cmd ACC/DEC | 0
P01.13 |  | Decel (Sec) |  |  | Good! | [11 empty] | P08.29 | PID Base SEL | 0
P02.00 |  | DI1:RUN/STOP, DI2:FWD/REV |  |  | Value? | [11 empty] | P08.31 | P Gain2 of PID | 1
P02.03 |  | DI3: LOC/REM |  |  | Default | [11 empty] | P08.32 | I Gain2 of PID | 1
P02.04 |  | DI4: Auto/Man |  |  | r.o. | [11 empty] | P08.33 | D Gain2 of PID | 0
[17 empty] | P08.65 | PID REF SEL | 0
[17 empty] | P08.66 | PID REF% | 37.9
[5 empty] | STUFF NOT USED IN OUR DEMO | [11 empty] | P08.67 | AUX PID REV MAX | 10
CO |  |  | PV |  |  |  |  | Sleep Mode |  |  | error deviation | [5 empty] | P08.68 | PID Hold By Err | 0
P08.07 | 0 | CO Delay | P08.08 | 0 | 4-20mA Det Time |  |  | P08.10 | 0 | Sleep Freq or % | P08.13 | 10 | PID Feedback error deviation level |  |  |  | P08.69 | I GAIN Disable | 0
P08.05 | 100 | CO Limit | P08.09 | 0 | 4-20mA Fault Treatment |  |  | P08.11 | 0 | Wake Freq or % | P08.14 | 5 | PID Feedback error deviation time |  |  |  | P08.70 | PID Enable Level | 5
P08.16 | 0 | CO Comp Type | P08.06 | 0 | PV value from coms |  |  | P08.12 | 0 | Sleep Time | Extras … | [5 empty] | P08.71 | Smart Start Freq | 0
P08.17 | 0 | CO Comp Value | P08.15 | 5 | PID FB Filter |  |  | P08.18 | 0 | Sleep Function | P08.67 | 10 | Limit reverese frequency, % of P01.00 |  |  |  | P08.72 | Smsrt Start Acc | 3
|  |  | Smat Start |  |  |  |  | P08.19 | 50 | Wake Integral Limit | P08.68 | 0 | PID deviation limit |  |  |  | P08.75 | PID Gain2 Sel | 0
SP |  |  | P08.70 | 5 | Smart Start level (%) |  |  | P08.22 | 0 | Wake up delay time | P08.69 | 0 | Integral Separation Level |  |  |  | P08.76 | PID Gain2 Err1 | 10
P08.66 | 50 | PID Target Value (SP) setting | P08.71 | 0 | Smart Start Freq (Hz) |  |  | PID2 Parameters |  |  | P08.78 | 0 | Allowed Reverse runing time after startup |  |  |  | P08.77 | PID Gain2 Err2 | 40
P08.27 | 0 | SP Accel/Decel | P08.72 | 3 | Smart Start accel time (S) |  |  | P08.75 | 0 | When to switch | [6 empty] | P08.78 | Rev After Start | 0
[8 empty] | P08.76 | 10 | Switch Deviation 1
[8 empty] | P08.77 | 40 | Switch Deviation 2
SP
PV
+
-
PID
MAN
AUTO
CO (%)
– – – – – – DISCLAIMER – – – – – – – THIS INFORMATION PROVIDED BY AUTOMATIONDIRECT.COM IS PROVIDED “AS IS” WITHOUT A GUARANTEE OF ANY KIND. We do not guarantee that it is suitable for your particular application, nor do we assume any responsibility for it’s use in your application. It is provided solely as an example and it is incumbent upon the user to determine the applicability of information/code, and to fully test it prior to use.
GS20(X) PID Config. Tool
I/O Usage:
DI1 = RUN/STOP
DI2 = FWD/REV
DI3 = LOC/REM
DI4 = Auto/Man
AI1 = PV
(P02.04)
Common PID Display Stuff:
Value Desc. Display
10: PID: PV (%) ......................"b"
11: AI1 (%) ............................"1."
12: AI2 (%) ............................"2."
16: DI ......................................"i"
42: PID: SP (%) ......................"h."
43: PID: Comp Value (%.........."o."
Note on P6: scale output 0-100%
Note on C7: Setpoint Source 0: Frequency Command (REM:P00.20=9, LOC:P00.30=9) 1: P08.66 Setting 2: Comms (RS-485) 3: Analog Input (P03.00, P03.01) 4: Comm Card 5: Keypad Pot knob (GS20 only, not GS20X)
Note on P7: 0: Direction cannot be changed (FWD or REV) 1: Direction can be changed (FWD and REV)
Note on I12: Integral Gain units: Sec Decreasing I Increases effect
Note on I13: Differential Gain units: Sec
Note on P13: PV Source: 0: no function 1: Negative via Analog input (P03.00, P03.01) 2: Negative via single phase input (PG/DI7) [Pulse in] 3: Negative via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 4: Positive via Analog input (P03.00, P03.01) 5: Positive via singel phase input (PG/DI7) [Pulse in] 6: Positive via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 7: Negative Feedback via Coms 8. Positive Feedback via coms
Note on I16: Max Operating Freq P01.00 x P08.04% Limits I portion of PID to prevent windup.
Note on I17: 0: Dependant 1: Independent
Note on I18: bit0 = 1: PID follows P00.23 for FWD/REV ctrl bit0 = 0: PID follows calc for FWD/REV bit1 = 1: two decimal places for Kp bit1 = 0: one decimal plac for Kp
Note on P18: 4: PID Setpoint 5: PID PV 13: PID Compensation Value
Note on C20: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Pot 8: Com Card 9: PID
Note on C21: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on C22: 0: Standard HOA 1: Drive Stops when switching between REM/LOC 2: Run with REMOTE settings when switching modes 3: Run with LOCAL settings when switching modes 4: Use LOCAL settings in LOCAL mode, REMOTE settings in REMOTE Mode
Note on C23: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Potentiometer 8: Com Card 9: PID
Note on C24: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on P24: 10: PID: PV (%) "b" 11: AI1 (%) "1." 12: AI2 (%) "2." 16: DI "d" 42: PID SP (%) "h." 43. PID Comp Value (%) "o." 44. PID CO (Hz) "b."
Note on C27: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C28: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C29: 0: No Function 1: DI1:FWD DI2 REV 2: DI1:R/S, DI2:REV/FWD 3: DI1:Run, DI2: REV/FWD, DI3:Stop 4: DI1:FWD, DI2:Stop QUICK 5: DI1: R/S, DI2:REV/FWD QUICK 6: DI1:RUN, DI2: REV/FWD, DI3:Stop
Note on C31: Auto/Man via DI P02.0x = 21
Note on C36: Filters CO Expressed as a delay time, 0 to 2.5 seconds
Note on G36: 0-3600.0 sec Detection time for abnormal PID Feedback 0 disables
Note on L36: P08.10 Sleep Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P36: error signal can deviate this much % for P08.14 time before drive issues fault 1-50.0 %
Note on C37: Limits Output to Max Oper Freq P01.00 x P08.05 %
Note on G37: What to do when a 4-20mA fault is detected (see P08.08) 0: Warn and continue 1: Fault, ramp to stop 2: Fault and coast to stop 3: Warn and operat at last freq
Note on L37: P08.11 Wake Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P37: Amount of time error signal can be out of bounds 0-300.00 sec
Note on C38: You can tweak CO using either a value or an analog input 0: Value in P08.17 1: Analog input
Note on G38: This is where coms writes PV, can be +/- 200%
Note on L38: P08.12 Sleep Time Sleep Duration
Note on C39: CO Comp Value -100-100% Modify CO by: Max PID Target Value)P01.00) * P08.17
Note on G39: Feedback Fiter Time (s)
Note on L39: 0: Monitor CO Hz 1: Monitor PV %
Note on P39: Limits how far a reverese command can go. Sometimes a little reverese is ok ...
Note on G40: Allows you to automatically ramp up to close to where you want to be then releases to regular PID.
Note on L40: Integral as been accumulating during sleep and can get quite large. This limits the accumulation so PID can re-start faster after sleep. P01.00 x P08.19%
Note on P40: PID output has to change by this amount before it will update the final output. Think of it as a hysteresis thing.
Note on L41: Adds hysteresis so noise doesn't cause wake/sleep/wake/sleep bouncing back and forth. See diagram in user manual 0-600 secs
Note on C42: This is where Coms puts Setpoint
Note on L42: PID can automatically switch between two diiferent sets of PID coefficients
Note on P42: Limits if Ouput can reverese for a short period after startup. Depends on P08.21
Note on C43: You can specify an acel/decel ramp for th setpoint. This is important when the SP is being controlled by coms or multi-setpoint so you don't get a suden jump in SP value.
Note on L43: 0: No Switching 1: Auto switch based on ouput frequency (CO) 2: auto switch based on deviation (error)

## Baseline
[15 empty] | Related Parameters |  |  | PID Parameters
[14 empty] | Factory Reset: |  |  | P08.00 | PID FBK SEL | 1
[14 empty] | P00.02 | Reset Drive Params | 10 | P08.01 | P Gain of PID | 1
[17 empty] | P08.02 | I Gain of PID | 1
[14 empty] | Motor: |  |  | P08.03 | D Gain of PID | 0
[11 empty] | P08.26 | 100 | Output Scaling | P05.01 | Motor1: FLA | 3.7 | P08.04 | Up Limit for I | 100
P08.65 | 0 | SP Source | [8 empty] | P08.21 | 0 | Direction Limit | P05.02 | Motor1: Power | 0.75 | P08.05 | PID Out-Limit % | 100
[14 empty] | P05.03 | Rated Speed (rpm) | 3450 | P08.06 | PID Fbk Value | 0
[14 empty] | P05.04 | Motor1: Poles | 2 | P08.07 | PID Out-Filter | 0
[17 empty] | P08.P08 | FBK Detect Time | 0
[5 empty] | P08.01 (P) | 1 | P | [6 empty] | Drive: |  |  | P08.09 | PID FBK Loss | 0
[5 empty] | P08.02 (I) | 1 | I | [6 empty] | P00.20 | REMOTE Freq Source (PID) | 0 | P08.10 | Sleep Point | 0
Motor: |  |  |  |  | P08.03 (D) | 0 | D |  |  |  | P08.00 | 1 | PV Source & FWD/REV Acting | P00.21 | REMOTE Run/Stop Source (DI) | 1 | P08.11 | Wake Point | 0
P05.01 | 3.7 | Motor1: FLA | [11 empty] | P00.29 | LOC/REM Operation | 4 | P08.12 | Sleep Time | 0
P05.02 | 0.75 | Motor1: Power | [11 empty] | P00.30 | LOCAL Freq Source (POT) | 7 | P08.13 | PID DEV. Level | 10
p05.03 | 3450 | Rated Speed (rpm) |  |  | P08.04 | 100 | Intergral Limit | [6 empty] | P00.31 | LOCAL Run/Stop Source (DI) | 0 | P08.14 | PID DEV. Time | 5
P05.04 | 2 | Motor1: Poles |  |  | P08.20 | 0 | PID Mode |  |  |  | PV Conditioning (using AI1): |  |  | P01.00 | Motor1: Max Freq (Hz) | 60 | P08.15 | PID FBK Filter | 5
[5 empty] | P08.23 | 2 | PID Ctrl |  |  |  | P03.00 | 5 | AI1 = PV | P01.07 | Motor1: Min Freq (Hz) | 0 | P08.16 | PID Offset Way | 0
Drive Control: | [10 empty] | P03.03 | 0 | AI1 Offset (%) | P01.12 | Acceleration (Sec) | 0.25 | P08.17 | PID Offset | 0
P00.20 | 0 | REMOTE Freq Source (PID) | [8 empty] | P03.11 | 100 | AI1 Gain (%) | P01.13 | Decel (Sec) | 0.25 | P08.18 | Source of Sleep | 0
P00.21 | 1 | REMOTE Run/Stop Source (DI) | [8 empty] | P03.15 | 0.25 | AI1 Filter (Sec) | P02.00 | DI1:RUN/STOP, DI2:FWD/REV | 2 | P08.19 | I Limit for Wake | 50
P00.29 | 4 | LOC/REM Operation | [11 empty] | P02.03 | DI3: LOC/REM | 56 | P08.20 | PID Mode | 0
P00.30 | 7 | LOCAL Freq Source (POT) | [8 empty] | Display: |  |  | P02.04 | DI4: Auto/Man | 21 | P08.21 | Diection Limit | 0
P00.31 | 0 | LOCAL Run/Stop Source (DI) | [8 empty] | P00.04 | 10 | User Display: PV (%) |  |  |  | P08.22 | Wake Delay Time | 0
P01.00 | 60 | Motor1: Max Freq (Hz) | [11 empty] | Display: |  |  | P08.23 | PID CTRL BIT | 2
P01.07 | 0 | Motor1: Min Freq (Hz) | [11 empty] | P00.04 | User Display | 10 | P08.26 | PID Neg.OutLmit% | 100
P01.12 | 0.25 | Acceleration (Sec) |  |  | Color Code: | [11 empty] | P08.27 | PID Cmd ACC/DEC | 0
P01.13 | 0.25 | Decel (Sec) |  |  | Good! | [11 empty] | P08.29 | PID Base SEL | 0
P02.00 | 2 | DI1:RUN/STOP, DI2:FWD/REV |  |  | Value? | [11 empty] | P08.31 | P Gain2 of PID | 1
P02.03 | 56 | DI3: LOC/REM |  |  | Default | [11 empty] | P08.32 | I Gain2 of PID | 1
P02.04 | 21 | DI4: Auto/Man |  |  | r.o. | [11 empty] | P08.33 | D Gain2 of PID | 0
[17 empty] | P08.65 | PID REF SEL | 0
[17 empty] | P08.66 | PID REF% | 37.9
[5 empty] | STUFF NOT USED IN OUR DEMO | [11 empty] | P08.67 | AUX PID REV MAX | 10
CO |  |  | PV |  |  |  |  | Sleep Mode |  |  | error deviation | [5 empty] | P08.68 | PID Hold By Err | 0
P08.07 | 0 | CO Delay | P08.08 | 0 | 4-20mA Det Time |  |  | P08.10 | 0 | Sleep Freq or % | P08.13 | 10 | PID Feedback error deviation level |  |  |  | P08.69 | I GAIN Disable | 0
P08.05 | 100 | CO Limit | P08.09 | 0 | 4-20mA Fault Treatment |  |  | P08.11 | 0 | Wake Freq or % | P08.14 | 5 | PID Feedback error deviation time |  |  |  | P08.70 | PID Enable Level | 0
P08.16 | 0 | CO Comp Type | P08.06 | 0 | PV value from coms |  |  | P08.12 | 0 | Sleep Time | Extras … | [5 empty] | P08.71 | Smart Start Freq | 5
P08.17 | 0 | CO Comp Value | P08.15 | 5 | PID FB Filter |  |  | P08.18 | 0 | Sleep Function | P08.67 | 10 | Limit reverese frequency, % of P01.00 |  |  |  | P08.72 | Smsrt Start Acc | 0
|  |  | Smat Start |  |  |  |  | P08.19 | 50 | Wake Integral Limit | P08.68 | 0 | PID deviation limit |  |  |  | P08.75 | PID Gain2 Sel | 0
SP |  |  | P08.70 | 5 | Smart Start level (%) |  |  | P08.22 | 0 | Wake up delay time | P08.69 | 0 | Integral Separation Level |  |  |  | P08.76 | PID Gain2 Err1 | 10
P08.66 | 50 | PID Target Value (SP) setting | P08.71 | 0 | Smart Start Freq (Hz) |  |  | PID2 Parameters |  |  | P08.78 | 0 | Allowed Reverse runing time after startup |  |  |  | P08.77 | PID Gain2 Err2 | 40
P08.27 | 0 | SP Accel/Decel | P08.72 | 3 | Smart Start accel time (S) |  |  | P08.75 | 0 | When to switch | [6 empty] | P08.78 | Rev After Start | 0
[8 empty] | P08.76 | 10 | Switch Deviation 1
[8 empty] | P08.77 | 40 | Switch Deviation 2
SP
PV
+
-
PID
MAN
AUTO
CO (%)
– – – – – – DISCLAIMER – – – – – – – THIS INFORMATION PROVIDED BY AUTOMATIONDIRECT.COM IS PROVIDED “AS IS” WITHOUT A GUARANTEE OF ANY KIND. We do not guarantee that it is suitable for your particular application, nor do we assume any responsibility for it’s use in your application. It is provided solely as an example and it is incumbent upon the user to determine the applicability of information/code, and to fully test it prior to use.
GS20(X) PID Config. Tool
I/O Usage:
DI1 = RUN/STOP
DI2 = FWD/REV
DI3 = LOC/REM
DI4 = Auto/Man
AI1 = PV
(P02.04)
Common PID Display Stuff:
Value Desc. Display
10: PID: PV (%) ......................"b"
11: AI1 (%) ............................"1."
12: AI2 (%) ............................"2."
16: DI ......................................"i"
42: PID: SP (%) ......................"h."
43: PID: Comp Value (%.........."o."
Note on P6: scale output 0-100%
Note on C7: Setpoint Source 0: Frequency Command (REM:P00.20=9, LOC:P00.30=9) 1: P08.66 Setting 2: Comms (RS-485) 3: Analog Input (P03.00, P03.01) 4: Comm Card 5: Keypad Pot knob (GS20 only, not GS20X)
Note on P7: 0: Direction cannot be changed (FWD or REV) 1: Direction can be changed (FWD and REV)
Note on I12: Integral Gain units: Sec Decreasing I Increases effect
Note on I13: Differential Gain units: Sec
Note on P13: PV Source: 0: no function 1: Negative via Analog input (P03.00, P03.01) 2: Negative via single phase input (PG/DI7) [Pulse in] 3: Negative via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 4: Positive via Analog input (P03.00, P03.01) 5: Positive via singel phase input (PG/DI7) [Pulse in] 6: Positive via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 7: Negative Feedback via Coms 8. Positive Feedback via coms
Note on I16: Max Operating Freq P01.00 x P08.04% Limits I portion of PID to prevent windup.
Note on I17: 0: Dependant 1: Independent
Note on I18: bit0 = 1: PID follows P00.23 for FWD/REV ctrl bit0 = 0: PID follows calc for FWD/REV bit1 = 1: two decimal places for Kp bit1 = 0: one decimal plac for Kp
Note on P18: 4: PID Setpoint 5: PID PV 13: PID Compensation Value
Note on C20: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Pot 8: Com Card 9: PID
Note on C21: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on C22: 0: Standard HOA 1: Drive Stops when switching between REM/LOC 2: Run with REMOTE settings when switching modes 3: Run with LOCAL settings when switching modes 4: Use LOCAL settings in LOCAL mode, REMOTE settings in REMOTE Mode
Note on C23: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Potentiometer 8: Com Card 9: PID
Note on C24: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on P24: 10: PID: PV (%) "b" 11: AI1 (%) "1." 12: AI2 (%) "2." 16: DI "d" 42: PID SP (%) "h." 43. PID Comp Value (%) "o." 44. PID CO (Hz) "b."
Note on C27: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C28: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C29: 0: No Function 1: DI1:FWD DI2 REV 2: DI1:R/S, DI2:REV/FWD 3: DI1:Run, DI2: REV/FWD, DI3:Stop 4: DI1:FWD, DI2:Stop QUICK 5: DI1: R/S, DI2:REV/FWD QUICK 6: DI1:RUN, DI2: REV/FWD, DI3:Stop
Note on C31: Auto/Man via DI P02.0x = 21
Note on C36: Filters CO Expressed as a delay time, 0 to 2.5 seconds
Note on G36: 0-3600.0 sec Detection time for abnormal PID Feedback 0 disables
Note on L36: P08.10 Sleep Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P36: error signal can deviate this much % for P08.14 time before drive issues fault 1-50.0 %
Note on C37: Limits Output to Max Oper Freq P01.00 x P08.05 %
Note on G37: What to do when a 4-20mA fault is detected (see P08.08) 0: Warn and continue 1: Fault, ramp to stop 2: Fault and coast to stop 3: Warn and operat at last freq
Note on L37: P08.11 Wake Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P37: Amount of time error signal can be out of bounds 0-300.00 sec
Note on C38: You can tweak CO using either a value or an analog input 0: Value in P08.17 1: Analog input
Note on G38: This is where coms writes PV, can be +/- 200%
Note on L38: P08.12 Sleep Time Sleep Duration
Note on C39: CO Comp Value -100-100% Modify CO by: Max PID Target Value)P01.00) * P08.17
Note on G39: Feedback Fiter Time (s)
Note on L39: 0: Monitor CO Hz 1: Monitor PV %
Note on P39: Limits how far a reverese command can go. Sometimes a little reverese is ok ...
Note on G40: Allows you to automatically ramp up to close to where you want to be then releases to regular PID.
Note on L40: Integral as been accumulating during sleep and can get quite large. This limits the accumulation so PID can re-start faster after sleep. P01.00 x P08.19%
Note on P40: PID output has to change by this amount before it will update the final output. Think of it as a hysteresis thing.
Note on L41: Adds hysteresis so noise doesn't cause wake/sleep/wake/sleep bouncing back and forth. See diagram in user manual 0-600 secs
Note on C42: This is where Coms puts Setpoint
Note on L42: PID can automatically switch between two diiferent sets of PID coefficients
Note on P42: Limits if Ouput can reverese for a short period after startup. Depends on P08.21
Note on C43: You can specify an acel/decel ramp for th setpoint. This is important when the SP is being controlled by coms or multi-setpoint so you don't get a suden jump in SP value.
Note on L43: 0: No Switching 1: Auto switch based on ouput frequency (CO) 2: auto switch based on deviation (error)

## Demo Copy
[15 empty] | Related Parameters |  |  | PID Parameters
[14 empty] | Factory Reset: |  |  | P08.00 | PID FBK SEL | 1
[14 empty] | P00.02 | Reset Drive Params | 10 | P08.01 | P Gain of PID | 1
[17 empty] | P08.02 | I Gain of PID | 1
[14 empty] | Motor: |  |  | P08.03 | D Gain of PID | 0
[11 empty] | P08.26 | 100 | Output Scaling | P05.01 | Motor1: FLA |  | P08.04 | Up Limit for I | 100
P08.65 | 0 | SP Source | [8 empty] | P08.21 | 0 | Direction Limit | P05.02 | Motor1: Power |  | P08.05 | PID Out-Limit % | 100
[14 empty] | P05.03 | Rated Speed (rpm) |  | P08.06 | PID Fbk Value | 0
[14 empty] | P05.04 | Motor1: Poles |  | P08.07 | PID Out-Filter | 0
[17 empty] | P08.P08 | FBK Detect Time | 0
[5 empty] | P08.01 (P) | 1 | P | [6 empty] | Drive: |  |  | P08.09 | PID FBK Loss | 0
[5 empty] | P08.02 (I) | 1 | I | [6 empty] | P00.20 | REMOTE Freq Source (PID) | 0 | P08.10 | Sleep Point | 0
Motor: |  |  |  |  | P08.03 (D) | 0 | D |  |  |  | P08.00 | 1 | PV Source & FWD/REV Acting | P00.21 | REMOTE Run/Stop Source (DI) |  | P08.11 | Wake Point | 0
P05.01 | 3.7 | Motor1: FLA | [11 empty] | P00.29 | LOC/REM Operation | 4 | P08.12 | Sleep Time | 0
P05.02 | 0.75 | Motor1: Power | [11 empty] | P00.30 | LOCAL Freq Source (POT) |  | P08.13 | PID DEV. Level | 10
p05.03 | 3450 | Rated Speed (rpm) |  |  | P08.04 | 100 | Intergral Limit | [6 empty] | P00.31 | LOCAL Run/Stop Source (DI) | 0 | P08.14 | PID DEV. Time | 5
P05.04 | 2 | Motor1: Poles |  |  | P08.20 | 0 | PID Mode |  |  |  | PV Conditioning (using AI1): |  |  | P01.00 | Motor1: Max Freq (Hz) | 60 | P08.15 | PID FBK Filter | 5
[5 empty] | P08.23 | 2 | PID Ctrl |  |  |  | P03.00 | 5 | AI1 = PV | P01.07 | Motor1: Min Freq (Hz) |  | P08.16 | PID Offset Way | 0
Drive Control: | [10 empty] | P03.03 | 0 | AI1 Offset (%) | P01.12 | Acceleration (Sec) |  | P08.17 | PID Offset | 0
P00.20 | 0 | REMOTE Freq Source (PID) | [8 empty] | P03.11 | 100 | AI1 Gain (%) | P01.13 | Decel (Sec) |  | P08.18 | Source of Sleep | 0
P00.21 | 1 | REMOTE Run/Stop Source (DI) | [8 empty] | P03.15 | 0.25 | AI1 Filter (Sec) | P02.00 | DI1:RUN/STOP, DI2:FWD/REV |  | P08.19 | I Limit for Wake | 50
P00.29 | 4 | LOC/REM Operation | [11 empty] | P02.03 | DI3: LOC/REM |  | P08.20 | PID Mode | 0
P00.30 | 7 | LOCAL Freq Source (POT) | [8 empty] | Display: |  |  | P02.04 | DI4: Auto/Man |  | P08.21 | Direction Limit | 0
P00.31 | 0 | LOCAL Run/Stop Source (DI) | [8 empty] | P00.04 | 10 | User Display: PV (%) |  |  |  | P08.22 | Wake Delay Time | 0
P01.00 | 60 | Motor1: Max Freq (Hz) | [11 empty] | Display: |  |  | P08.23 | PID CTRL BIT | 2
P01.07 | 0 | Motor1: Min Freq (Hz) | [11 empty] | P00.04 | User Display |  | P08.26 | PID Neg.OutLmit% | 100
P01.12 | 0.25 | Acceleration (Sec) |  |  | Color Code: | [11 empty] | P08.27 | PID Cmd ACC/DEC | 0
P01.13 | 0.25 | Decel (Sec) |  |  | Good! | [11 empty] | P08.29 | PID Base SEL | 0
P02.00 | 2 | DI1:RUN/STOP, DI2:FWD/REV |  |  | Value? | [11 empty] | P08.31 | P Gain2 of PID | 1
P02.03 | 56 | DI3: LOC/REM |  |  | Default | [11 empty] | P08.32 | I Gain2 of PID | 1
P02.04 | 21 | DI4: Auto/Man |  |  | r.o. | [11 empty] | P08.33 | D Gain2 of PID | 0
[17 empty] | P08.65 | PID REF SEL | 0
[17 empty] | P08.66 | PID REF% | 37.9
[17 empty] | P08.67 | AUX PID REV MAX | 10
[5 empty] | STUFF NOT USED IN OUR DEMO | [11 empty] | P08.68 | PID Hold By Err | 0
CO |  |  | PV |  |  |  |  | Sleep Mode |  |  | error deviation | [5 empty] | P08.69 | I GAIN Disable | 0
P08.07 | 0 | CO Delay | P08.08 | 0 | 4-20mA Det Time |  |  | P08.10 | 0 | Sleep Freq or % | P08.13 | 10 | PID Feedback error deviation level |  |  |  | P08.70 | PID Enable Level | 5
P08.05 | 100 | CO Limit | P08.09 | 0 | 4-20mA Fault Treatment |  |  | P08.11 | 0 | Wake Freq or % | P08.14 | 5 | PID Feedback error deviation time |  |  |  | P08.71 | Smart Start Freq | 0
P08.16 | 0 | CO Comp Type | P08.06 | 0 | PV value from coms |  |  | P08.12 | 0 | Sleep Time | Extras … | [5 empty] | P08.72 | Smsrt Start Acc | 3
P08.17 | 0 | CO Comp Value | P08.15 | 5 | PID FB Filter |  |  | P08.18 | 0 | Sleep Function | P08.67 | 10 | Limit reverese frequency, % of P01.00 |  |  |  | P08.75 | PID Gain2 Sel | 0
|  |  | Smat Start |  |  |  |  | P08.19 | 50 | Wake Integral Limit | P08.68 | 0 | PID deviation limit |  |  |  | P08.76 | PID Gain2 Err1 | 10
SP |  |  | P08.70 | 5 | Smart Start level (%) |  |  | P08.22 | 0 | Wake up delay time | P08.69 | 0 | Integral Separation Level |  |  |  | P08.77 | PID Gain2 Err2 | 40
P08.66 | 50 | PID Target Value (SP) setting | P08.71 | 0 | Smart Start Freq (Hz) |  |  | PID2 Parameters |  |  | P08.78 | 0 | Allowed Reverse runing time after startup |  |  |  | P08.78 | Rev After Start | 0
P08.27 | 0 | SP Accel/Decel | P08.72 | 3 | Smart Start accel time (S) |  |  | P08.75 | 0 | When to switch
[8 empty] | P08.76 | 10 | Switch Deviation 1
[8 empty] | P08.77 | 40 | Switch Deviation 2
SP
PV
+
-
PID
MAN
AUTO
CO (%)
– – – – – – DISCLAIMER – – – – – – – THIS INFORMATION PROVIDED BY AUTOMATIONDIRECT.COM IS PROVIDED “AS IS” WITHOUT A GUARANTEE OF ANY KIND. We do not guarantee that it is suitable for your particular application, nor do we assume any responsibility for it’s use in your application. It is provided solely as an example and it is incumbent upon the user to determine the applicability of information/code, and to fully test it prior to use.
GS20(X) PID Config. Tool
I/O Usage:
DI1 = RUN/STOP
DI2 = FWD/REV
DI3 = LOC/REM
DI4 = Auto/Man
AI1 = PV
(P02.04)
Common PID Display Stuff:
Value Desc. Display
10: PID: PV (%) ......................"b"
11: AI1 (%) ............................"1."
12: AI2 (%) ............................"2."
16: DI ......................................"i"
42: PID: SP (%) ......................"h."
43: PID: Comp Value (%.........."o."
Note on P7: scale output 0-100%
Note on C8: Setpoint Source 0: Frequency Command (REM:P00.20=9, LOC:P00.30=9) 1: P08.66 Setting 2: Comms (RS-485) 3: Analog Input (P03.00, P03.01) 4: Comm Card 5: Keypad Pot knob (GS20 only, not GS20X)
Note on P8: 0: Direction cannot be changed (FWD or REV) 1: Direction can be changed (FWD and REV)
Note on I13: Integral Gain units: Sec Decreasing I Increases effect
Note on I14: Differential Gain units: Sec
Note on P14: PV Source: 0: no function 1: Negative via Analog input (P03.00, P03.01) 2: Negative via single phase input (PG/DI7) [Pulse in] 3: Negative via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 4: Positive via Analog input (P03.00, P03.01) 5: Positive via singel phase input (PG/DI7) [Pulse in] 6: Positive via singel phase input (PG/DI7) [Pulse in] withut direction (P10.16 = 5, DI7) 7: Negative Feedback via Coms 8. Positive Feedback via coms
Note on I17: Max Operating Freq P01.00 x P08.04% Limits I portion of PID to prevent windup.
Note on I18: 0: Dependant 1: Independent
Note on I19: bit0 = 1: PID follows P00.23 for FWD/REV ctrl bit0 = 0: PID follows calc for FWD/REV bit1 = 1: two decimal places for Kp bit1 = 0: one decimal plac for Kp
Note on P19: 4: PID Setpoint 5: PID PV 13: PID Compensation Value
Note on C21: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Pot 8: Com Card 9: PID
Note on C22: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on C23: 0: Standard HOA 1: Drive Stops when switching between REM/LOC 2: Run with REMOTE settings when switching modes 3: Run with LOCAL settings when switching modes 4: Use LOCAL settings in LOCAL mode, REMOTE settings in REMOTE Mode
Note on C24: 0: Keypad 1: RD-485 2: AI (See P3.00) 3: External Up/Down terminal 4: Pulse In (DI7) w/o direction 7: Keypad Potentiometer 8: Com Card 9: PID
Note on C25: 0: Keypad 1: DI 2: RS-485 5: Com Card
Note on P25: 10: PID: PV (%) "b" 11: AI1 (%) "1." 12: AI2 (%) "2." 16: DI "d" 42: PID SP (%) "h." 43. PID Comp Value (%) "o." 44. PID CO (Hz) "b."
Note on C28: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C29: Something small so accel doesn't imped PID, typically 0.25 sec or smaller
Note on C30: 0: No Function 1: DI1:FWD DI2 REV 2: DI1:R/S, DI2:REV/FWD 3: DI1:Run, DI2: REV/FWD, DI3:Stop 4: DI1:FWD, DI2:Stop QUICK 5: DI1: R/S, DI2:REV/FWD QUICK 6: DI1:RUN, DI2: REV/FWD, DI3:Stop
Note on C32: Auto/Man via DI P02.0x = 21
Note on C38: Filters CO Expressed as a delay time, 0 to 2.5 seconds
Note on G38: 0-3600.0 sec Detection time for abnormal PID Feedback 0 disables
Note on L38: P08.10 Sleep Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P38: error signal can deviate this much % for P08.14 time before drive issues fault 1-50.0 %
Note on C39: Limits Output to Max Oper Freq P01.00 x P08.05 %
Note on G39: What to do when a 4-20mA fault is detected (see P08.08) 0: Warn and continue 1: Fault, ramp to stop 2: Fault and coast to stop 3: Warn and operat at last freq
Note on L39: P08.11 Wake Freq Can be Freq or Hz, depending on P08.18 0-599.0 HZ 0-200.00%
Note on P39: Amount of time error signal can be out of bounds 0-300.00 sec
Note on C40: You can tweak CO using either a value or an analog input 0: Value in P08.17 1: Analog input
Note on G40: This is where coms writes PV, can be +/- 200%
Note on L40: P08.12 Sleep Time Sleep Duration
Note on C41: CO Comp Value -100-100% Modify CO by: Max PID Target Value)P01.00) * P08.17
Note on G41: Feedback Fiter Time (s)
Note on L41: 0: Monitor CO Hz 1: Monitor PV %
Note on P41: Limits how far a reverese command can go. Sometimes a little reverese is ok ...
Note on G42: Allows you to automatically ramp up to close to where you want to be then releases to regular PID.
Note on L42: Integral as been accumulating during sleep and can get quite large. This limits the accumulation so PID can re-start faster after sleep. P01.00 x P08.19%
Note on P42: PID output has to change by this amount before it will update the final output. Think of it as a hysteresis thing.
Note on L43: Adds hysteresis so noise doesn't cause wake/sleep/wake/sleep bouncing back and forth. See diagram in user manual 0-600 secs
Note on C44: This is where Coms puts Setpoint
Note on L44: PID can automatically switch between two diiferent sets of PID coefficients
Note on P44: Limits if Ouput can reverese for a short period after startup. Depends on P08.21
Note on C45: You can specify an acel/decel ramp for th setpoint. This is important when the SP is being controlled by coms or multi-setpoint so you don't get a suden jump in SP value.
Note on L45: 0: No Switching 1: Auto switch based on ouput frequency (CO) 2: auto switch based on deviation (error)

## Sheet3
Industry Terms | GS20 Terminology
(SP) Setpoint | PID Target Value or PID command
(MAN) Man Mode | PID Function Disable
error | Deviation
(CO) Control Output | frequency command
(PV) Process Variable | Feedback Signal
REM (Remote) | AUTO
LOC (Local) | HAND
Forward/Reverse acting vs positive negative
Missing:
Bumpless
Ability to set sample time
Consistent terminology
PV Min/Max (must do in %)
Simple Man/Auto switching